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[bookmark: _Toc161140796]INTRODUCTION AND SUMMARY OF THE BID SOLICITATION
This Bid Solicitation is issued by the Department of the Treasury, Division of Purchase and Property (Division), Procurement Bureau, on behalf of the New Jersey Department of Transportation (NJDOT), Statewide Agencies, and Cooperative Purchasing Participants. Quotes submitted in response to this Bid Solicitation shall be through the State of New Jersey’s eProcurement system, NJSTART.  Bidders are advised to thoroughly read all sections of this Bid Solicitation and follow all instructions.  

Bidders are strongly encouraged to visit the NJSTART Vendor Support Page, which contains Quick Reference Guides (QRGs), supporting videos, a glossary of NJSTART terms, and helpdesk contact information.  Bidders should utilize the QRGs before attempting to submit a Quote through NJSTART.   It is the Bidder’s responsibility to ensure that the Quote and attachments have been properly submitted.  Inquiries concerning the use of NJSTART may be directed to njstart@treas.nj.gov. The Division will not respond to substantive questions related to the Bid Solicitation or any other Contract via this email address.

[bookmark: _Toc400531467][bookmark: _Toc428533937][bookmark: _Toc32310614][bookmark: _Toc161140797]1.1    PURPOSE AND INTENT
The purpose of this Bid Solicitation is to solicit Quotes for Traffic Signals, Poles, Controls, Electrical Equipment and Signal Indications and Warning Devices.

It is the intent of the State to award Contracts to those responsible Bidders whose Quotes, conforming to this Bid Solicitation are most advantageous to the State of New Jersey (State), price and other factors considered.  The State may award any or all price lines.  The State, however, reserves the right to separately procure individual requirements that are the subject of the Contract during the Contract term, when deemed by the Director of the Division (Director) to be in the State’s best interest.

There are 154 Price Lines, which are itemized as follows:

	Price Line #
	
Description

	Group 1 - Price Lines 1 and 2

	1
	Traffic Signal Indication Parts Replacement Visors – 8 Inch, as per NJDOT Spec. # BME-TS-Visor, Dated April 28, 2010

	2
	Traffic Signal Indication Parts Replacement Visors – 12 Inch, as per NJDOT Spec. # BME-TS-Visor, Dated April 28, 2010

	Individual Price Lines -  Price Lines 3 and 4

	3
	Traffic Signal Indication Parts Scoop Visor – 12 Inch, as per NJDOT Spec. # BME-TS-Scoop Visor, Dated May 31, 2018

	4
	Geometrically Programmed Louver, Plastic 12 Inch Indication as per NJDOT Spec. & NJDOT Sketch # 1 (Attachment #5), Pelco GL-1010 Only - NO SUBSTITUTIONS

	Group 2 - Price Lines 5 and 6

	5
	Traffic Signal Indication Parts Traffic Signal Indication - 8 Inch (Housing Only) as per NJDOT Spec. Dated April 26, 2007 Drawing BME-TS-Head

	6
	Traffic Signal Indication Parts Traffic Signal Indication - 12 Inch (Housing Only) as per NJDOT Spec. No. BME-TS-Head Dated April 26, 2007

	Individual Price Lines -  Price Lines 7 and 8

	7
	Traffic Signal Indication Parts Traffic Signal Indication - Hand/Man (Housing Only) 16" X 18" as per NJDOT Spec. No. BME-TS-Hand/Man Dated May 25, 2010

	8
	Traffic Signal Indication/Parts Visor Screen (Egg Crate) for 16 "X 18" Indication as per NJDOT Spec. No. BME-TS-VSEC Dated May 31, 2018

	Group 3 - Price Lines 9 and 10

	9
	Traffic Signal Indication/Parts 3M-R.A.G. (3 Section – 12 Inch) as per NJDOT Spec. Drawing EB-TS-2

	10
	Traffic Signal Indication/Parts 3M - Arrow  (1 Section) as per NJDOT Spec. Drawing EB-TS-2

	Individual Price Lines -  Price Lines 11 through 30

	11
	Traffic Signal Hangers Brackets Sign Bracket, as per 2007 Standard Electrical Details T-4507 

	12
	Traffic Signal Hangers Brackets Sign Bracket Offset Type, as per 2007 Standard Electrical Details T-4507

	13
	Traffic Signal Hangers Brackets Adapter- Pedestal (Slip Fitter) with Brass Chase Nipple as per 2007 Standard Electrical Details T-0607 and T-0707

	14
	Traffic Signal Hangers Brackets Adapter- Pedestal (Offset Slip Fitter) with Brass Chase Nipple as per NJDOT Sketch #2 (Attachment #5) 

	15
	Traffic Signal Hangers Brackets Band Bracket Assembly- Mid Arm 8-12” Indication 2007 Standard Electrical  Details T-2107, Pelco AS-116-3-29-SS Only - NO SUBSTITUTIONS

	16
	Traffic Signal Hanger Bracket Cable Bracket Assembly – Mid Arm 8-12” Indication 2007 Standard Electrical Details T-2107, Pelco AS-125-3-29-SS Only - NO SUBSTITUTIONS

	17
	Traffic Signal Hanger Bracket Band Bracket Assembly – Mid Arm- 8-12” Indication 2007 Standard Electrical Details T-2107, Pelco AS-103-3-29-SS Only - NO SUBSTITUTIONS

	18
	Traffic Signal Hanger Bracket Cable Bracket Assembly- Mid Arm 8 -12” Indication 2007 Standard Electrical Details T-2107, Pelco AS-151-3-29-SS Only - NO SUBSTITUTIONS

	19
	Traffic Signal Hangers Brackets Clevis- H Mast Arms 2007 Standard Electrical Details T-0407 Universal  Joint 

	20
	Traffic Signal Hangers Brackets Mast Arm Slip Fitter 2007 Standard Electrical Details T-0407 Mast Arm Slip Fitter 

	21
	Traffic Signal Hangers Brackets Universal Joint & Wire Outlet with SS Hardware 2007 Standard Electrical Details T-0407 Universal Joint and Wire Outlet

	22
	Traffic Signal Hangers Brackets Pedestrian Hinge Clamp Assembly for Approx. 7-1/2” Diameter Pole with 12” Standard Nipple 2007 Standard Electrical Details T-0607

	23
	Traffic Signal Hangers Brackets Pedestrian Hinge Clamp Assembly for Approx. 9-1/2” Diameter Pole with 12” Standard Nipple, 2007 Standard Electrical Details T-0607

	24
	Traffic Signal Hangers Brackets Pedestrian Cast Clamp Assembly for Approx. 9-1/2” Diameter Pole with 12” Standard Nipple, 2007 Standard Electrical Details T-0607

	25
	Traffic Signal Hangers Brackets Pedestrian Cast Clamp for Approx. 9-1/2” Diameter Pole with 12” Standard Nipple, 2007 Standard Electrical Details T-0607

	26
	Traffic Signal Hangers Brackets Two-Way Bracket Assembly with T-Bar 2007 Standard Electrical Details T-0507 Hollow Spider for 2-Way Assembly & T-Bar 

	27
	Traffic Signal Hangers Brackets Three-Way Bracket Assembly 2007 Standard Electrical Details T-0507 Hollow Spider for 3-Way Assembly

	28
	Traffic Signal Hangers Brackets Four-Way Bracket Assembly 2007 Standard Electrical Details T-0507 Hollow Spider for 4-Way Assembly

	29
	Traffic Signal Hangers Brackets Pole Clamp Assembly, Hinge Strap Type with 12” Standard Nipple, 2007 Standard Electrical Details T-0607 Pole Clamp Assembly, Hinge Strap Type

	30
	Traffic Signal Hangers Brackets Traffic Signal Safety Chain 2007 Standard Electrical Details T-0307 and T-0907

	Group 4 - Price Lines 31 through 64

	31
	Traffic Signal Poles, Arms, Bases Paint Adder for Poles and Arms Only – Up to and including 23 feet in length 

	32
	Traffic Signal Poles, Arms, Bases Paint Adder for Poles and Arms Only – Over 23 feet in Length

	33
	Traffic Signal Pole & Lighting Pole Bases Paint Adder for Bases Only

	34
	Traffic Signal Hangers Brackets TB-20 Base 2007 Standard Electrical Details T-0207

	35
	Traffic Signal Hangers Brackets HHB Base 2007 Standard Electrical Details T-1507

	36
	Traffic Signal Hangers Brackets K Base 2007 Standard Electrical Details T-1007

	37
	Traffic Signal Hangers Brackets Traffic Signal Pole Type T-2007 Standard Electrical Details T-0107

	38
	Traffic Signal Hangers Brackets Traffic Signal Pole Type C 2007 Standard Electrical Details T-0807

	39
	Traffic Signal Hangers Brackets Traffic Signal Pole Type K 2007 Standard Electrical Details T -1007

	40
	Traffic Signal Hangers Brackets Pedestal Pole – 8 Foot 2007 Standard Electrical Details T-0707

	41
	Traffic Signal Hangers Brackets Pedestal Pole – 12 Foot 2007 Standard Electrical Details T-0707

	42
	Traffic Signal Hangers Brackets Traffic Signal Standard, Type KE 2007 Standard Electrical Details T -1007

	43
	Traffic Signal Pole, Type KE Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch #3 (Attachment #5)

	44
	Traffic Signal Poles, Arms, Bases Traffic Signal Pole Type K - Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch #4 (Attachment #5)

	45
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – Trombone 15 ft. as per NJDOT Drawing T-1207

	46
		Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – Trombone 20 ft. as per NJDOT Drawing T-1207




	47
		Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm –15 ft. as per NJDOT Drawing T-0307




	48
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 20 ft. as per NJDOT Drawing T-0307

	49
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 25 ft. as per NJDOT Drawing T-0307

	50
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 15 ft. Type K as per NJDOT Drawing T-0907

	51
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 20 ft. – Type K as per NJDOT Drawing T-0907

	52
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 25 ft. – Type K as per NJDOT Drawing T-0907

	53
	Traffic Signal Poles, Arms, Bases Traffic Signal Standard Type T Pole Cap as per NJDOT Drawing T-0107

	54
	Traffic Signal Poles, Arms, Bases Traffic Signal Standard Type K Pole Cap as per NJDOT Drawing T-1007 Detail C

	55
	Paint Adder Poles, Arms, Lighting Poles, Arms

	56
	Lighting  Poles, Arms, Bases Lighting Pole,  Type L as per NJDOT Spec. Drawing P-0189

	57
	Lighting Poles, Arms, Bases Lighting  Pole, Type L-40 as per NJDOT Spec. Drawing P-0289

	58
	Lighting Poles, Arms, Bases Lighting Arm, 8 Foot as per NJDOT Spec. Drawing P-0389

	59
	Lighting Poles, Arms, Bases Lighting Arm, 15 Foot as per NJDOT Spec. Drawing P-0389

	60
	Lighting Poles, Arms, Bases Transformer Base (Lighting) as per NJDOT Spec. Drawing L-2107

	61
	Lighting Poles, Arms, Bases, Lighting Pole, 22 Foot Bridge Mounted Pole – Flagpoles Inc. #RTA8M22AABXV-HH, Arm In Line with Hand Hole 12 inches from Bottom with Vibration Dampener, Flagpoles #RTA8M22AABXV-HH  Only - NO SUBSTITUTIONS

	62
	Lighting Poles, Arms, Bases, Lighting Pole, 37 Foot Bridge Mounted Pole - Flagpoles Inc. #RTA8X37AABXV-HH, Arm In Line with Hand Hole 12 inches From Bottom with Vibration Dampener, Flagpoles #RTA8X37AABXV-HH Only - NO SUBSTITUTIONS

	63
	Lighting Poles, Arms, Bases Lighting Arm Assembly as per NJDOT Sketch #5 (Attachment #5)

	64
	Lighting Poles, Arm, Bases Mounting Adapter for Offset Luminaire as per NJDOT Drawing L -1807

	Group 5 - Price Lines 65 through 78

	65
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Standard Type S (Includes Anchorage) with Alternate Pole Top as per Bid Solicitation Specifications and NJDOT Detail T-1107 & T-4307 and Reference Sketch #3 and Sketch #4 (Attachment #5)

	66
		Steel Traffic Signal Poles and Arms Steel Traffic Signal Standard Type SC (Includes Anchorage) with Alternate 
Pole Top as per Bid Solicitation Specifications and NJDOT Detail T-1107 & T-4307 and Reference 
Sketch #3 and Sketch #4 (Attachment #5)




	67
	Traffic Signal Poles, Arms, Bases Steel Traffic Signal Arm - 20 ft. as per NJDOT Drawing T-1307

	68
	Traffic Signal Poles, Arms, Bases Steel Traffic Signal Arm - 25 ft. as per NJDOT Drawing T-1307

	69
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Arm - 30 ft. as per NJDOT Drawing T-1307

	70
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Arm- 35 ft. as per NJDOT Drawing T-1307

	71
	Steel Traffic Signal Poles and Arms, Bases Steel Traffic Signal Arm- 40 ft. as per NJDOT Drawing T-1307

	72
	Steel Traffic Signal Poles and  Arms, Bases Steel Traffic Signal Arm- 45 ft. as per NJDOT Drawing T-1307

	73
	Steel Traffic Signal Poles and Arms, Bases Steel Traffic Signal Arm- 50 ft. as per NJDOT Drawing T-1307

	74
	Steel Traffic Signal Poles and Arms, Steel Traffic Signal Standard, Type SC Lighting Arm - 15 ft., as per NJDOT Drawing T -1307

	75
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Standard, Type SC Lighting Arm - 20 ft., as per NJDOT  Drawing T-1307

	76
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Anchorages as per NJDOT Drawing T-4307

	77
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Type S - Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch # 4

	78
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Type SC -Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch # 4

	Group 6 - Price Lines 79 through 88

	79
	Paint Adder Cabinet - Up to and Including 23 Feet in Length, as per Bid Solicitation Sections 4.7 and 4.23 for Cabinets and Cabinet Hardware

	80
	Paint Adder Cabinet - Over  23 Feet in Length, as Per Bid Solicitation Sections 4.7 and 4.23 Cabinets and Cabinet Hardware 

	81
	Cabinets and Cabinet Hardware Meter Cabinet, Type T As Per NJDOT Spec. Drawing P -0489, and NJDOT Drawing T-4307

	82
	Cabinets and Cabinet Hardware Meter Cabinet Type T (Sheet Metal), as per NJDOT Spec. Drawing T -3507

	83
	Cabinets and Cabinet Hardware Meter Cabinet, Fabricated Typed (53 Inch), as per NJDOT Sketch #11 (Attachment #5)

	84
	Cabinets and Cabinet Hardware Meter Cabinet Type M (Sheet Metal), as per NJDOT Spec. Drawing L -1407

	85
	Cabinets and Cabinet Hardware Cabinet Type P, as per NJDOT Sketch #6 (Attachment #5)

	86
	Cabinets and Cabinet Hardware Cabinet Type P Split Skirt, as per NJDOT Sketch #7 (Attachment #5)

	87
		Cabinets and Cabinet Hardware Cabinet, Type P Skirt, as per NJDOT Sketch #7 (Attachment #5)




	88
		Cabinets and Cabinet Hardware Meter Cabinet Type M  - Lock & Keys, as per NJDOT Spec. Drawing L -1407




	Individual Price Lines - Price Lines 89 and 90

	89
	Cabinets and Cabinet Hardware Meter Cabinet, Composite Carlon Part #C2420A4 Only - NO SUBSTITUTIONS

	90
	Cabinets and Cabinet Hardware Controller Cabinet, Lock & Keys S591, as per NJDOT Sketch #8  (Attachment #5), CCL Products A55481RS: Right Hand, Dead Bolt Only - NO SUBSTITUTIONS

	Group 7 - Price Lines 91 through 95

	91
	Signs/ Sign Brackets Sign – Red Signal Ahead – LED, as per NJDOT Spec. Drawing T -1407

	92
	Signs/Sign Brackets – Blankout Sign LED “No Left Turn”, as per NJDOT Drawing T-1407 & Sketch #10 (Attachment #5)

	93
	Signs/Sign Brackets – Blankout Sign LED “No Right Turn”, as per NJDOT Drawing T-1407 & Sketch #10 (Attachment #5)

	94
	Signs/Sign Brackets – Blankout Sign LED “No Turn On Red” 2007 Standard Electrical Detail T -1407, as per NJDOT Drawing T-1407,BME – LED-NTBLO Dated 5/31/2018 & NJDOT Sketch #10 (Attachment #5)

	95
	Signs/Sign Brackets – Blankout Sign LED (Message To Be Determined When Ordering) 2007 Standard Electrical Detail T -1407, as per NJDOT Drawing T-1407, BME  LED-NTBLO Dated 5/31/2018 & Sketch #10 (Attachment #5)

	Individual Price Lines- Price Lines 96 through 100

	96
	Signal Control Devices, Detector (Microwave), as per NJDOT Spec. Drawing Model TC-26B

	97
	Signal Control Devices, Detector (Microwave), as per NJDOT Spec. Drawing Model TC-30

	98
	Signal Control Devices, Loop Detector – 4 Channel, as per NJDOT Spec. EB-LD-3

	99
	Signal Control Devices, Detector Card, as per NJDOT Spec. EB-LD-CARD

	100
	Signal Control Devices, Uninterruptible Power System- 850 Watts, as per NJDOT Spec. #BME-UPS-1, Dated 9/22/2014

	Group 8 - Price Lines 101 and 102

	101
	Miscellaneous Signal Products Devices, Wireless Transceiver System-2, Including All Mounting Hardware, Antennas, Connectors, Cables for a Complete System, as per NJDOT Spec. BME-WCCS, Dated 5/24/10

	102
	Miscellaneous Signal Products Devices, Wireless Transceiver System-3, Including All Mounting Hardware, Antennas, Connectors, Cables for a Complete System, as per NJDOT Spec. BME-WCCS, Dated 5/24/10

	Group 9 – Price Lines 103 and 104

	103
	Miscellaneous Signal Products Devices, Backplate – 8” Signal Head, as per NJDOT Drawing T-1807

	104
	Miscellaneous Signal Products Devices, Backplate – 12” Signal Head, as per NJDOT Drawing T-1807

	Group 10 - Price Lines 105 through 108

	105
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base TB-20, as per NJDOT Drawing T-0207

	106
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base K, as per NJDOT Drawing T-0707

	107
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base TB-30, as per NJDOT Drawing L-1507

	108
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base TB-17, as per NJDOT Drawing L-2107

	Group 11 - Price Lines 109 through 111

	109 
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Econolite 5 Inch Border Aluminum, Black Non-Louvered 3 Section with 3 Inch 3M Tape Border - Econolite P43-01 Only - NO SUBSTITUTIONS

	110
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Econolite 5 Inch Border, Aluminum, Black Non-Louvered 4 Section with 3 Inch 3M Tape Border - Econolite P44-01 Only - NO SUBSTITUTIONS

	111
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Econolite 5 Inch Border, Aluminum, Black Non-Louvered 5 Section with 3 Inch 3M Tape Border - Econolite P45-01 Only - NO SUBSTITUTIONS

	Group 12 - Price Lines 112 through 114

	112
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, McCain Aluminum Black Non-Louvered 3 Section with 3 Inch 3M Tape Border - McCain HP Only - NO SUBSTITUTIONS

	113
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, McCain Aluminum Black Non-Louvered 4 Section with 3 Inch 3M Tape Border - McCain HP Only - NO SUBSTITUTIONS

	114
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Mccain Aluminum Black Non-Louvered 5 Section with 3 Inch 3M Tape Border - McCain HP Only - NO SUBSTITUTIONS

	Individual Price Lines – Price Lines 115 and 116

	115
	Miscellaneous Signal Products Devices, GPS Time Reference - Garmin Only - NO SUBSTITUTIONS

	116
	Miscellaneous Signal Products Devices, GPS Time Reference - Eltec Time Sync 1-GPS Only - NO SUBSTITUTIONS

	Group 13 - Price Lines 117 through 121

	117
	Traffic Signals and Equipment Traffic Signal Cable 2/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	118
	Traffic Signals and Equipment Traffic Signal Cable 5/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	119
	 Traffic Signals and Equipment Traffic Signal Cable 7/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	120
	Traffic Signals and Equipment Traffic Signal Cable 10/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	121
	Traffic Signals and Equipment Traffic Signal Cable 14/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	Group 14 - Price Lines 122 and 123

	122
	Hand/Man Pedestrian Signal Head, as per NJDOT Spec. BMEO-LED-H/M-PSH- Dated: 09/16/2014 and Bid Solicitation Specifications

	123
	Hand/Man Pedestrian Signal Head, as per NJDOT Spec. BMEO-LED-H/M-PSM- Dated: 09/16/2014 and Bid Solicitation Specifications

	  Group 15 - Price Lines 124 through 126

	124
	Red, Amber, Green LED Module for Optically Programmed Traffic Signal Red Module, as per NJDOT Spec. BMEO-OP-RAG Dated 01/16/2014 and Bid Solicitation Specifications

	125
	Red, Amber, Green LED Module for Optically Programmed Traffic Signal Amber Module, as per NJDOT Spec. BMEO-OP-RAG Dated 01/16/2014 and Bid Solicitation Specifications

	126
	Red, Amber, Green LED Module for Optically Programmed Traffic Signal Green Module, as per NJDOT Spec. BMEO-OP-RAG Dated 01/16/2014 and Bid Solicitation Specifications

	Individual Price Lines – Price Lines 127 and 128

	127
	Indication LED Solar Beacon Assembly 12” Amber, as per NJDOT Spec. BMEO-LED-SFB Dated 09/16/2014 and Bid Solicitation Specifications

	128
	Adjustable Face Vehicle Traffic Control Aluminum Signal Head (Housing Only 3-12” Sections), as per NJDOT Spec. BMEO-TSH-AL, Dated 1/16/2014 and the Bid Solicitation Specifications

	Individual Price Lines - Price Lines 129 through 139

	129
	Lighting Poles Arms, Bases Black Lighting Arm Assembly as per NJDOT Sketch #12 (Attachment #5)

	130
	Generator Auxiliary Cabinet (GAC) as per Bose GAC-Alpha Dated January 24, 2024, Alpha Only - NO SUBSTITUTIONS

	131
	Generator Auxiliary Cabinet (GAC), as per Bose-GAC-Other Dated January 24, 2024

	132
	Audible Push Button System 8 APS and Control Unit – Polara INS23TNO-Y WITH iCCU-S2 Only - NO SUBSTITUTIONS

	133
	Audible Push Button System 8 APS and Control Unit – Campbell WiAAPS APC 501-0910C - NO SUBSTITUTIONS

	134
	Pedestrian Pole Assembly, as per NJDOT Sketch #13 (Attachment #5) Only - NO SUBSTITUTIONS

	135
	Pedestrian Pole Assembly, as per NJDOT Sketch #13 (Attachment #5)

	136
	Traffic Signal Pole Assembly, as per NJDOT Sketch #14 (Attachment #5) Only - NO SUBSTITUTIONS

	137
	Traffic Signal Pole Assembly, as per NJDOT Sketch #14 (Attachment #5)

	138
	Econolite Cobalt Signal Controller - NO SUBSTITUTIONS

	139
	Trafficware Commander Signal Controller - NO SUBSTITUTIONS

	Individual Price Lines – Percentage Discount or Markup from the Brand Manufacturer’s Price List/Catalog Pricing - Price Lines 140 through 154

	140
	Polara Brand Only – Price List - NO SUBSTITUTIONS

	141
	General Fasteners (Any Brand) – Price List 

	142
	Campbell Brand Only – Price List - NO SUBSTITUTIONS

	143
	Econolite Signal Controller Brand Only – Price List - NO SUBSTITUTIONS

	144
	Trafficware Signal Controller Brand Only – Price List - NO SUBSTITUTIONS

	145
	Gridsmart Brand Only – Price List - NO SUBSTITUTIONS

	146
	Miovision Brand Only – Price List - NO SUBSTITUTIONS

	147
	Wavetronix Brand Only – Price List - NO SUBSTITUTIONS

	148
	2-Way Assemblies Components - Pelco Inc. Brand Only - Price List  - NO SUBSTITUTIONS

	149
	Audible Push Button System Components – Polara Brand Only – Price List - NO SUBSTITUTIONS

	150
	Audible Push Button System Components - Campbell Brand Only – Price List - NO SUBSTITUTIONS

	151
	Aeroflex Back Plate - Pelco Inc. Brand Only  - Price List - NO SUBSTITUTIONS

	152
	Alpha Brand Only – Price List - NO SUBSTITUTIONS

	153
	1-Way Assemblies Components - Pelco Inc. Brand Only – Price List - NO SUBSTITUTIONS

	154
	Beacon-4-Life Brand Only – Price List - NO SUBSTITUTIONS






The State intends to make awards as follows:

For Groups 1 through 15:

For Groups 1 through 15 the State intends to make one (1) Contract award per Group.

Bidders must bid on all price lines contained within the Group.  If a Bidder does not bid on all price lines within the Group, its Quote will be considered non-responsive for that Group.

A Bidder is not required to bid on all Groups on the State-Supplied Price Sheet in order to be considered responsive.  

Price line items are grouped for Quote evaluation purposes only.  Upon Contract award, Using Agencies will be able to order any price lines within the Groups individually.

For Individual Price Lines – Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139:  

The Bid Solicitation contains Individual Price Lines, identified as Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139 on the State-Supplied Price Sheet.  A Bidder may bid on one, some or all Individual Price Lines (Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139).  A Bidder is not required to bid on all Individual Price Lines on the State-Supplied Price Sheet in order to be considered responsive.

For each individual price line, the State intends to make one (1) Contract award.

For Individual Price Lines – Price Lines 140 through 154:  

A Bidder may bid on one, some or all Individual Price Lines for Price Lines 140 through 154.  A Bidder is not required to bid on all Individual Price Lines on the State-Supplied Price Sheet in order to be considered responsive.

For individual price lines 140 through 154, the State intends to make a Contract award to all responsive Bidders.

This Bid Solicitation is not designated as a Small Business or Disabled Veteran-Owned Business set aside. 

The State of New Jersey Standard Terms and Conditions (SSTCs) included with this Bid Solicitation will apply to all Contracts made with the State.  These terms are in addition to the terms and conditions set forth in this Bid Solicitation and should be read in conjunction with them unless the Bid Solicitation specifically indicates otherwise.  

[bookmark: _Toc400531468][bookmark: _Toc428533938][bookmark: _Toc32310615][bookmark: _Toc161140798]1.2    BACKGROUND 
This is a reprocurement of the products under Traffic Signals, Poles, Controls, Electrical Equipment, and LED Devices.  Bidders interested in reviewing the current Contract specifications and pricing information may do so by following the instruction below.  Bidders should not rely upon or use data or information from the contract when preparing a response to this Bid Solicitation as this Bid Solicitation addresses the State’s current requirements. 
· Go to: www.njstart.gov 
· Select “Active Blankets”
· In the search bar, select “Blankets” from the drop down menu
· Enter the T1529 and click “[image: ]”
· The current Contract list will appear under “Results”

[bookmark: _Toc161140799]1.3    CONTRACT AMOUNT
The estimated amount of the Contract, if stated, shall not be construed as either the maximum or minimum amount which the State shall be obliged to order.

[bookmark: _Toc400531506][bookmark: _Toc428533977][bookmark: _Toc32310702][bookmark: _Toc161140800]1.4    ORDER OF PRECEDENCE OF CONTRACTUAL TERMS
The Contract awarded, and the entire agreement between the parties, as a result of this Bid Solicitation shall consist of:  (1) the final Bid Solicitation, (2) the State of New Jersey Standard Terms and Conditions, (3) the Quote, and if applicable (4) any Bidder responses to clarifications; (5) a Bidder’s Best and Final Offer, (6) other negotiated document, and/or (7) third party document.  In the event of a conflict in the terms and conditions among the documents comprising this Contract, the order of precedence, for purposes of interpretation thereof, listed from highest ranking to lowest ranking as noted above. 

Any other terms or conditions, not included with the Bidder’s Quote and accepted by the State, shall not be incorporated into the Contract awarded.  Any references to external documentation, including those documents referenced by a URL, including without limitation, technical reference manuals, technical support policies, copyright notices, additional license terms, etc., are subject to the terms and conditions of the Bid Solicitation and the State of New Jersey Standard Terms and Conditions.  In the event of any conflict between the terms of a document incorporated by reference, the terms and conditions of the Bid Solicitation and the State of New Jersey Standard Terms and Conditions shall prevail.

[bookmark: _Toc161140801]1.5    INTRASTATE COOPERATIVE PURCHASING
The State intends to extend the Contracts awarded to the State's Intrastate Cooperative Purchasing Participants.  Although the State is making the use of any Contract resulting from this Bid Solicitation available to Intrastate Cooperative Purchasing Participants, the State makes no representation as to the acceptability of the Bid Solicitation’s terms and conditions to any Intrastate Cooperative Purchasing Participants.



[bookmark: _Toc161140802]PRE-QUOTE SUBMISSION INFORMATION
The Bidder assumes sole responsibility for the complete effort required in submitting a Quote and for reviewing the Quote submission requirements and the Scope of Work requirements.  

[bookmark: _ELECTRONIC_QUESTION_AND][bookmark: _Toc428533940][bookmark: _Toc32310617][bookmark: _Toc161140803]2.1    ELECTRONIC QUESTION AND ANSWER PERIOD
The Division will electronically accept questions and inquiries from all potential Bidders via the “Q&A” Tab of the Bid Solicitation in NJSTART.  Questions should be directly tied to a Bid Solicitation Section, the Price Sheet, Form or Attachment; and should reference the specific Bid Solicitation Section or document to which it relates.

The cut-off date for electronic questions and inquiries relating to this Bid Solicitation is indicated on the Bid Solicitation cover page.  In the event that questions are posed by Bidders, answers to such questions will be issued by Bid Amendment.  
[bookmark: _1.3.3__Mandatory_Pre-Bid_Conference][bookmark: _1.3.5__SUBMISSION_OF_BID_PROPOSAL][bookmark: _1.3.2_SUBMISSION_OF_BID_PROPOSAL]
A Bidder shall not contact the Using Agency and/or the Procurement Specialist directly, in person, by telephone or by e-mail, concerning this Bid Solicitation, prior to Contract award.

[bookmark: _Toc161140804]2.2    EXCEPTIONS TO THE STATE OF NJ STANDARD TERMS AND CONDITIONS (SSTC)
Questions regarding the State of New Jersey Standard Terms and Conditions and exceptions to mandatory requirements MUST be posed during the Electronic Question and Answer period and shall contain the Bidder’s suggested changes and the reason(s) for the suggested change(s).

[bookmark: _Toc161140805]2.3    BID AMENDMENTS
In the event that it becomes necessary to clarify or revise this Bid Solicitation, such clarification or revision will be by Bid Amendment.  Any Bid Amendment will become part of this Bid Solicitation and part of any Contract awarded. Bid Amendments will be posted as a file attachment on the “Summary” page of the Bid Solicitation in NJSTART after the cut-off date.  

There are no designated dates for release of Bid Amendments.  Those Bidders who are on the bid holder list either through commodity code registration in NJSTART or by acknowledging the bid in NJSTART should receive notification of any Bid Amendment(s). If a Bidder is not on the bid holder list, Bid Amendments are still viewable on the “Summary” page of the Bid Solicitation in NJSTART.

It is the sole responsibility of the Bidder to be knowledgeable of all Bid Amendments related to this procurement. An interested Bidder should check the NJSTART “Open Bids” Tab on a daily basis to ensure review of the most updated information.

[bookmark: _1.3.4_MANDATORY/OPTIONAL_SITE][bookmark: _1.3.45_MANDATORY/OPTIONAL_SITE][bookmark: _MANDATORY/OPTIONAL_SITE_VISIT][bookmark: _Toc224543885][bookmark: _Toc238623352][bookmark: _Toc400531474][bookmark: _Toc428533944][bookmark: _Toc32310620][bookmark: _Toc161140806]2.4    MANDATORY/OPTIONAL SITE VISIT
Not applicable to this procurement.

[bookmark: _1.3.5__MANDATORY/OPTIONAL][bookmark: _1.3.6__MANDATORY/OPTIONAL][bookmark: _MANDATORY/OPTIONAL_PRE-QUOTE_CONFER][bookmark: _Toc224543888][bookmark: _Toc238623354][bookmark: _Toc428533945][bookmark: _Toc32310621][bookmark: _Toc161140807]2.5    MANDATORY/OPTIONAL PRE-QUOTE CONFERENCE
Not applicable to this procurement.

[bookmark: _Toc95619434][bookmark: _Toc109701220][bookmark: _Toc225321579][bookmark: _Toc400531476][bookmark: _Toc428533946][bookmark: _Toc32310622][bookmark: _Toc161140808][bookmark: _Toc94946029][bookmark: _Toc72744593]2.6    PRE-QUOTE DOCUMENT REVIEW 
Not applicable to this procurement.

[bookmark: _QUOTE_SUBMISSION_REQUIREMENTS][bookmark: _Toc161140809]QUOTE SUBMISSION REQUIREMENTS

[bookmark: _Toc161140810]3.1    QUOTE SUBMISSION 
In order to be considered for award, the Quote must be received electronically by the Division’s Proposal Review Unit, through NJSTART, by the required date and time. 

The date and time of the Quote opening are indicated on the Bid Solicitation cover sheet and on the “Summary” Tab of the Bid Solicitation webpage within NJSTART.  If the Quote opening deadline has been revised, the new Quote opening deadline will be shown on the posted Bid Amendment and on the “Summary” Tab of the Bid Solicitation webpage within NJSTART.  Quotes not received prior to the Quote opening deadline shall be rejected.

Quotes will be publicly opened and announced by telephone conference on the date and time of the quote opening. 
(Dial-in phone number: 888-204-5984 / Access code: 2602305)

When submitting a Quote through NJSTART, do not use any symbols (i.e., #, @, $, &, *) in the filename as this may prevent the Quote from being properly uploaded.  Uploaded files must be compatible with Microsoft Office and/or Adobe software applications. DO NOT UPLOAD files with extensions such as .zip, .numbers, or .pages.

When uploading the documents to NJSTART, the Bidder should select the “Confidential” option in NJSTART for attachments on the “Attachments” Tab to request that the documents not be displayed publicly through NJSTART. Marking an attachment as "Confidential" in NJSTART shall not constitute the Bidder's designation of the attachment as exempt from public disclosure under the New Jersey Open Public Records Act (OPRA), N.J.S.A. 47:1A-1 et seq., or the common law right to know.

[bookmark: _Toc161140811]3.2    BIDDER RESPONSIBILITY
The Bidder assumes sole responsibility for the complete effort required in submitting a Quote in response to this Bid Solicitation.  No special consideration will be given after Quotes are opened because of a Bidder’s failure to be knowledgeable as to all of the requirements of this Bid Solicitation.  The State assumes no responsibility and bears no liability for costs incurred by a Bidder in the preparation and submittal of a Quote in response to this Bid Solicitation or any pre-contract award costs incurred.

[bookmark: _Toc161140812]3.3    ANNOUNCEMENT OF QUOTE INFORMATION
On the date and time Quotes are due under the Bid Solicitation, all information concerning the Quotes submitted may be publicly announced and shall be available for inspection and copying except otherwise noted:  
A. Information appropriately designated as proprietary and/or confidential in a Bidder’s Quote shall not be available for inspection and copying; and
B. Where negotiation is contemplated, only the names and addresses of the Bidders submitting Quotes will be announced, and the contents of the Quotes shall not be available for inspection and copying until the Notice of Intent to Award is issued by the Director. 

[bookmark: _Toc161140813]3.4    QUOTE ERRORS
In accordance with N.J.A.C. 17:12-2.11 “Proposal errors,” a Bidder may withdraw its Quote as described below.

[bookmark: _Toc161140814]3.5    QUOTE WITHDRAWAL PRIOR TO QUOTE OPENING
A Bidder may withdraw its Quote submission in NJSTART prior to the Quote opening; however, Bidders should note that while withdrawn NJSTART Quotes remain viewable by the Bidder on its Vendor Profile Homepage, they are removed from the Division’s view and cannot be considered for Contract award. The Bidder may submit a revised Quote as long as the Quote is received prior to the announced date and time for Quote submission. Bidders may refer to the QRG “Submit a Quote” for additional instructions.

[bookmark: _Toc161140815]3.6    QUOTE WITHDRAWAL AFTER QUOTE OPENING, BUT PRIOR TO CONTRACT AWARD
If, after the Quote opening, but before Contract award, a Bidder discovers an error in its Quote, the Bidder may make a written request to the Procurement Bureau to withdraw its Quote, or a portion thereof, from consideration for award.  If the Bidder’s request to withdraw is made in good faith, and the State will not be significantly prejudiced by granting the withdrawal of the Quote beyond the loss of the benefit of the bargain to the State of the withdrawing Bidder’s offer, the request shall be granted.  Evidence of the Bidder’s good faith in making this request can be demonstrated by one (1) or more of the following factors: A mistake is so significant that to enforce the Contract resulting from the Quote would be unconscionable; that the mistake relates to a material feature or term of the Contract; and that the mistake occurred notwithstanding the Bidder’s exercise of reasonable care.  After Quote opening, while pursuant to the provisions of this section a Bidder may request to withdraw its Quote and the Director may in his/her discretion allow said Bidder to withdraw it, the Division also may take notice of repeated or unusual requests to withdraw by a Bidder and take those prior requests to withdraw into consideration when evaluating the Bidder’s future Quotes.

The Quote withdrawal request must include the Bid Solicitation Number, Bid Solicitation Title, and the Quote submission date and should be sent to Procurement.Bureau@treas.nj.gov.

If, during a Quote evaluation process, an obvious pricing error made by a potential Contract awardee is found, the Director or his/her designee shall issue written notice to the Bidder.  The Bidder will have up to five (5) business days after receipt of the notice to confirm its pricing.  If the Bidder fails to respond, its Quote shall be considered withdrawn, and no further consideration shall be given to it.

[bookmark: _Toc161140816]3.7    JOINT VENTURE
If a Joint Venture is submitting a Quote, the agreement between the parties relating to such Joint Venture should be submitted with the Joint Venture’s Quote.  Authorized signatories from each party comprising the Joint Venture must sign the Offer and Acceptance Page.  Each party to the Joint Venture must individually complete and comply with all the forms and certification requirements in Bid Solicitation Section 3 – Quote Submission Requirements. 

[bookmark: _Toc161140817]3.8    SMALL BUSINESS SET-ASIDE CONTRACTS
Not applicable to this procurement.

[bookmark: _Toc161140818]3.9    DISABLED VETERANS’ BUSINESS SET-ASIDE CONTRACT 
Not applicable to this procurement.

[bookmark: _Toc161140819]3.10    BID SECURITY
Not applicable to this procurement.

[bookmark: _Toc161140820]3.11    BIDDER ADDITIONAL TERMS SUBMITTED WITH THE QUOTE
A Bidder may submit additional terms as part of its Quote.  Additional terms are Bidder-proposed terms or conditions that do not conflict with the scope of work required in this Bid Solicitation, the terms and conditions of this Bid Solicitation, or the State of New Jersey Standard Terms and Conditions.  Bidder proposed terms or conditions that conflict with those contained in the State of New Jersey Standard Terms and Conditions will render a Quote non-responsive.  It is incumbent upon the Bidder to identify and remove its conflicting proposed terms and conditions prior to Quote submission.  

Quotes including Bidder proposed additional terms may be accepted, rejected, or negotiated, in whole or in part, at the State’s sole discretion. 

If Bidder intends to propose terms and conditions that conflict with the State of New Jersey Standard Terms and Conditions, those Bidder proposed terms and conditions shall only be considered if submitted and agreed to pursuant to the electronic question and answer procedure.  Bidders shall not submit exceptions or modifications as part of the Quote or on the “Terms and Conditions” Tab through NJSTART. 

[bookmark: _Toc161140821]3.12    QUOTE CONTENT
The Quote should be submitted with the attachments organized in the following manner:
· Forms
· State-Supplied Price Sheet

A Bidder should not password protect any submitted documents. Use of URLs in a Quote should be kept to a minimum and shall not be used to satisfy any material term of a Bid Solicitation. If a preprinted or other document included as part of the Quote contains a URL, a printed copy of the information should be provided and will be considered as part of the Quote. 

[bookmark: _Toc161140822]3.13    FORMS, REGISTRATIONS AND CERTIFICATIONS TO BE SUBMITTED WITH QUOTE 
A Bidder is required to complete and submit the following forms.  As an alternative to uploading certain forms with the submitted Quote, a Bidder may complete several certifications electronically in NJSTART on the “Terms and Categories” Tab within the Vendor Profile.  Those forms that may be completed on the NJSTART “Terms and Categories” Tab are noted below. Additionally, a Bidder may attach completed forms to the Vendor Profile.  Refer to QRGs “Vendor Forms” and “Attaching Files” for additional instructions.  VENDOR QUICK REFERENCE GUIDES

[bookmark: _Toc161140823]3.13.1    OFFER AND ACCEPTANCE PAGE 
The Bidder should complete and submit the Offer and Acceptance Page with the Quote.  The Offer and Acceptance Page must be signed by an authorized representative of the Bidder.  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) business days of the State’s request or the State may deem the Quote non-responsive.    

[bookmark: _Toc161140824]3.13.2    OWNERSHIP DISCLOSURE FORM 
Pursuant to N.J.S.A. 52:25-24.2, in the event the Bidder is a corporation, partnership or limited liability company, the Bidder must disclose all 10% or greater owners by (a) completing and submitting the Ownership Disclosure Form with the Quote; (b) if the Bidder has submitted a signed and accurate Ownership Disclosure Form dated and received no more than six (6) months prior to the Quote submission deadline for this procurement, the Division may rely upon that form; however, if there has been a change in ownership within the last six (6) months, a new Ownership Disclosure Form must be completed, signed and submitted with the Quote; or, (c) a Bidder with any direct or indirect parent entity which is publicly traded may submit the name and address of each publicly traded entity and the name and address of each person that holds a 10 percent or greater beneficial interest in the publicly traded entity as of the last annual filing with the federal Securities and Exchange Commission or the foreign equivalent, and, if there is any person that holds a 10 percent or greater beneficial interest, also shall submit links to the websites containing the last annual filings with the federal Securities and Exchange Commission or the foreign equivalent and the relevant page numbers of the filings that contain the information on each person that holds a 10 percent or greater beneficial interest. N.J.S.A. 52:25-24.2.
NOTE: In lieu of completing and submitting the paper-based form, the Bidder has the option to complete this form online in NJSTART on the “Terms and Categories” Tab.  

A Bidder’s failure to submit the information required by N.J.S.A. 52:25-24.2 will result in the rejection of the Quote as non-responsive and preclude the award of a Contract to said Bidder.

[bookmark: _Toc161140825]3.13.3    DISCLOSURE OF INVESTMENT ACTIVITIES IN IRAN FORM
The Bidder should  submit Disclosure of Investment Activities in Iran form to certify that, pursuant to N.J.S.A. 52:32-58, neither the Bidder, nor one (1) of its parents, subsidiaries, and/or affiliates (as defined in N.J.S.A. 52:32-56(e)(3)), is listed on the Department of the Treasury’s List of Persons or Entities Engaging in Prohibited Investment Activities in Iran and that neither the Bidder, nor one (1) of its parents, subsidiaries, and/or affiliates, is involved in any of the investment activities set forth in N.J.S.A. 52:32-56(f).  If the Bidder is unable to so certify, the Bidder shall provide a detailed and precise description of such activities as directed on the form.  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) business days of the State’s request or the State may deem the Quote non-responsive.
NOTE: In lieu of completing and submitting the paper-based form, the Bidder has the option to complete this certification online in NJSTART on the “Terms and Categories” Tab.  

[bookmark: _Toc161140826]3.13.4    DISCLOSURE OF INVESTIGATIONS AND OTHER ACTIONS INVOLVING BIDDER FORM
The Bidder should submit the Disclosure of Investigations and Other Actions Involving Bidder Form,  with its Quote, to provide a detailed description of any investigation, litigation, including administrative complaints or other administrative proceedings, involving any public sector clients during the past five (5) years, including the nature and status of the investigation, and, for any litigation, the caption of the action, a brief description of the action, the date of inception, current status, and, if applicable, disposition.  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) business days of the State’s request or the State may deem the Quote non-responsive.
NOTE: In lieu of completing and submitting the paper-based form, the Bidder has the option to complete this certification online in NJSTART on the “Terms and Categories” Tab.  

[bookmark: _Toc161140827]3.13.5    MACBRIDE PRINCIPLES FORM
The Bidder should submit the MacBride Principles Form.  Pursuant to N.J.S.A. 52:34-12.2, a Bidder is required to certify  that it either has no ongoing business activities in Northern Ireland and does not maintain a physical presence therein or that it will take lawful steps in good faith to conduct any business operations it has in Northern Ireland in accordance with the MacBride principles of nondiscrimination in employment as set forth in N.J.S.A. 52:18A-89.5 and in conformance with the United Kingdom’s Fair Employment (Northern Ireland) Act of 1989, and permit independent monitoring of their compliance with those principles.  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) business days of the State’s request or the State may deem the Quote non-responsive.
NOTE: In lieu of completing and submitting the paper-based form, the Bidder has the option to complete this certification online in NJSTART on the “Terms and Categories” Tab.  

[bookmark: _Toc161140828]3.13.6    SERVICE PERFORMANCE WITHIN THE UNITED STATES
Not applicable to this procurement.

[bookmark: _Toc161140829]3.13.7    CONFIDENTIALITY/COMMITMENT TO DEFEND
Pursuant to the New Jersey Open Public Records Act (OPRA), N.J.S.A. 47:1A-1 et seq., or the common law right to know, Quotes can be released to the public in accordance with N.J.A.C. 17:12-1.2(b) and (c).  

The Bidder should submit a completed and signed Confidentiality/Commitment to Defend Form with the Quote.  In the event that the Bidder does not submit the Confidentiality form with the Quote, the State reserves the right to request that the Bidder submit the form after Quote submission.

After the opening of sealed Quotes, all information submitted by a Bidder in response to a Bid Solicitation is considered public information notwithstanding any disclaimers to the contrary submitted by a Bidder.  Proprietary, financial, security and confidential information may be exempt from public disclosure by OPRA and/or the common law when the Bidder has a good faith, legal/factual basis for such assertion. 

When the Bid Solicitation contains a negotiation component, the Quote will not be subject to public disclosure until a notice of intent to award a Contract is announced. 

As part of its Quote, a Bidder may request that portions of the Quote be exempt from public disclosure under OPRA and/or the common law. The Bidder must provide a detailed statement clearly identifying those sections of the Quote that it claims are exempt from production, and the legal and factual basis that supports said exemption(s) as a matter of law.  The State will not honor any attempts by a Bidder to designate its price sheet, price list/catalog, and/or the entire Quote as proprietary and/or confidential, and/or to claim copyright protection for its entire Quote.  If the State does not agree with a Bidder’s designation of proprietary and/or confidential information, the State will use commercially reasonable efforts to advise the Bidder. Copyright law does not prohibit access to a record which is otherwise available under OPRA.

The State reserves the right to make the determination as to what to disclose in response to an OPRA request.  Any information that the State determines to be exempt from disclosure under OPRA will be redacted.  

In the event of any challenge to the Bidder’s assertion of confidentiality that is contrary to the State’s determination of confidentiality, the Bidder shall be solely responsible for defending its designation, but in doing so, all costs and expenses associated therewith shall be the responsibility of the Bidder. The State assumes no such responsibility or liability.  

In order not to delay consideration of the Quote or the State’s response to a request for documents, the State requires that Bidder respond to any request regarding confidentiality markings within the timeframe designated in the State’s correspondence regarding confidentiality.  If no response is received by the designated date and time, the State will be permitted to release a copy of the Quote with the State making the determination regarding what may be proprietary or confidential.

[bookmark: _Toc161140830]3.13.8    SUBCONTRACTOR UTILIZATION PLAN
Bidders intending to use Subcontractor(s) shall list all subcontractors on the Subcontractor Utilization Plan form or may list the Subcontractor(s) on the “Subcontractor” Tab in NJSTART. 

For a Quote that does NOT include the use of any Subcontractors, the Bidder is automatically certifying that, if selected for an award, the Bidder will be performing all work required by the Contract. 

If it becomes necessary for the Contractor to substitute a Subcontractor, add a Subcontractor, or substitute its own staff for a Subcontractor, the Contractor will identify the proposed new Subcontractor or staff member(s) and the work to be performed.  The Contractor shall forward a written request to substitute or add a Subcontractor or to substitute its own staff for a Subcontractor to the State Contract Manager for consideration.    The Contractor must provide a completed Subcontractor Utilization Plan, a detailed justification documenting the necessity for the substitution or addition, and resumes of its proposed replacement staff or of the proposed Subcontractor’s management, supervisory, and other key personnel that demonstrate knowledge, ability and experience relevant to that part of the work which the Subcontractor is to undertake. The qualifications and experience of the replacement(s) must equal or exceed those of similar personnel proposed by the Contractor in its Quote.  The State Contract Manager will forward the request to the Director for approval.  

NOTE: No substituted or additional Subcontractors are authorized to begin work until the Contractor has received written approval from the Director.

0.   SMALL BUSINESS AND/OR DISABLED VETERANS’ BUSINESS SUBCONTRACTING SET-ASIDE CONTRACT 
Not applicable to this procurement.

[bookmark: _Toc161140831]3.13.9    RESERVED

[bookmark: _Toc161140832]3.13.10    AFFIRMATIVE ACTION
The intended Contractor and its named Subcontractor(s) must submit a copy of a New Jersey Certificate of Employee Information Report, or a copy of Federal Letter of Approval verifying it is operating under a federally approved or sanctioned Affirmative Action program.  If the Contractor and/or its named Subcontractor(s) are not in possession of either a New Jersey Certificate of Employee Information Report or a Federal Letter of Approval, it/they must complete and submit the Affirmative Action Employee Information Report (AA-302).  Information, instruction and the application are available at https://www.state.nj.us/treasury/contract_compliance/index.shtml.

[bookmark: _Toc161140833]3.13.11    RESERVED

[bookmark: _Toc161140834]3.13.12    STATE OF NEW JERSEY SECURITY DUE DILIGENCE THIRD-PARTY INFORMATION SECURITY QUESTIONNAIRE 
Not applicable to this procurement.

[bookmark: _Toc161140835]3.13.13    BUSINESS REGISTRATION
[bookmark: OLE_LINK1]In accordance with N.J.S.A. 52:32-44(b), a Bidder and its named Subcontractors must have a valid Business Registration Certificate (“BRC”) issued by the Department of the Treasury, Division of Revenue and Enterprise Services prior to the award of a Contract.  A Bidder should verify its Business Registration Certification Active status on the “Maintain Terms and Categories” Tab within its profile in NJSTART. In the event of an issue with a Bidder’s Business Registration Certification Active status, NJSTART provides a link to take corrective action. 

[bookmark: _Toc161140836]3.13.14    Certification of Non-Involvement in Prohibited Activities in Russia or Belarus Pursuant to P.L.2022, c.3
The Bidder should submit the Certification of Non-Involvement in Prohibited Activities in Russia or Belarus Form.  Pursuant to P.L.2022, c.3, a person or entity seeking to enter into or renew a contract for the provision of goods or services shall certify that it is not Engaging in Prohibited Activities in Russia or Belarus as defined by P.L.2002, c.3, sec. 1(e).  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) business days of the State’s request or the State may deem the Quote non-responsive.
[bookmark: _Toc161140837]3.14    TECHNICAL QUOTE 
Not applicable to this procurement.

[bookmark: _Toc161140838]3.15    BIDDER QUOTE OVERVIEW FORM
Not applicable to this procurement.

[bookmark: _BIDDER_DATA_SHEET/FORM][bookmark: _Toc161140839]3.16    BIDDER DATA SHEET/FORM
The Bidder should submit the Bidder Data Sheet with its Quote.  The Bidder Data Sheet will be used to evaluate the Bidder’s ability to complete the Scope of Work.  

The Bidder should provide in its response to Part I of the Bidder Data Sheet all relevant information regarding its experience in successfully completing contracts of a similar size and scope to the work required by this Bid Solicitation.  

The Bidder must provide, in Part II of the Bidder Data Sheet, details of any negative actions taken by other contracting entities against it in the course of performing these projects including, but not limited to, receipt of letters of potential default, default, cure notices, termination of services for cause, or other similar notifications/processes.  Additionally, the Bidder should provide details, including any negative audits, reports, or findings by any governmental agency for which the Bidder is/was the contractor on any contracts of similar scope.  In the event a Bidder neglects to include this information in its Quote, the Bidder’s omission of necessary disclosure information may be cause for rejection of the Bidder’s Quote by the State.

If proposing to use a Subcontractor, the Bidder should provide as an attachment to the Bidder Data Sheet documented experience to demonstrate that each Subcontractor has successfully performed work on contracts of a similar size and scope to the work that the Subcontractor is designated to perform in the Bidder’s Quote.  The Bidder must provide a detailed description of services to be provided by each Subcontractor.  

[bookmark: _Toc161140840]3.17    AFFIDAVIT OF APPAREL PRODUCTION
Not applicable to this procurement.

[bookmark: _Toc161140841]3.18    DISCLOSURE OF PRODUCT COMPOSITION
Not applicable to this procurement.

[bookmark: _Toc161140842]3.19    SPECIFICATION DATA SHEETS
Not applicable to this procurement.

[bookmark: _Toc161140843]3.20    SAMPLES AND TESTING
Not applicable to this procurement.

[bookmark: _SPECIFICATION_CONFORMANCE_FORM][bookmark: _Toc161140844]3.21    SPECIFICATION CONFORMANCE FORM
The Bidder shall submit with its Quote the Specification Conformance Form.  By submitting this form, the Bidders certifies that all items offered in response to this Bid Solicitation conform to the requirements set forth in the Bid Solicitation. 

[bookmark: _Toc161140845]3.22    MANUFACTURER’S CERTIFICATION
Upon the State’s request, the Bidder should submit a letter of certification from the manufacturer whose product is supplied, certifying that the Bidder is authorized by the manufacturer to supply the good(s) specified.  The certification must indicate that the Bidder was authorized by the manufacturer to supply the good(s) specified as of the Quote Opening Date. The State reserves the right to request such certification and to require that such certification be provided within five (5) business days from the time it is requested.  

[bookmark: _Toc161140846]3.23    MANUFACTURER’S PUBLISHED LIST OF OPTIONS AND ATTACHMENTS/PRICE LIST
Not applicable to this procurement.

[bookmark: _Toc161140847]3.24    PRICE LIST AND/OR CATALOG
For Price Lines 140 through 154, a Bidder should submit a preprinted price list or catalog for each Price Line and brand bid. The price list and/or catalog submitted must clearly indicate the products and brand offered and the firm, fixed pricing associated with the products, such that the applicable Bid Solicitation price line may be determined.  

To avoid any confusion, the price list provided by the Bidder for the brand bid should only contain one price column, to which the discount or markup bid on the State-Supplied Price Sheet will be applied.

The Bidder acknowledges that any references to, minimum orders, order threshold charges, service charges, price escalation clauses, sales or other applicable taxes,  FOB shipping point limitations, additional terms and conditions and shipping charges, contained in the preprinted price lists, catalogs, and/or literature, shall not apply or become part of any Contract awarded as a result of this Bid Solicitation. 

If a price list is not published, then the prices listed on the Bidder’s letterhead, dated and with authorized signature are acceptable.  The letter should include the Bid Solicitation number.

If a Bidder does not provide a preprinted price list or catalog for each Price Line/brand bid with its Quote, the State reserves the right to request such information from the Bidder.  The Bidder must respond to such request by providing all requested information within forty-eight (48) hours.  If the information requested is not received within forty-eight (48) hours, the Quote may be deemed non-responsive.

The State intends to publish the price list and/or catalog provided to the Attachments tab of the Contract in NJSTART.

[bookmark: _Toc161140848]3.25     MANAGEMENT OVERVIEW
Not applicable to this procurement.

[bookmark: _Toc161140849]3.26    CONTRACT MANAGEMENT
Not applicable to this procurement.

[bookmark: _Toc161140850]3.27    CONTRACT SCHEDULE
Not applicable to this procurement.

[bookmark: _Toc161140851]3.28     MOBILIZATION PLAN
Not applicable to this procurement.

[bookmark: _Toc161140852]3.29    ADDITIONAL PLAN(S)
Not applicable to this procurement.

[bookmark: _Toc161140853]3.30    ORGANIZATIONAL EXPERIENCE
Not applicable to this procurement.

[bookmark: _Toc161140854]3.31    LOCATION
Not applicable to this procurement.

[bookmark: _Toc161140855]3.32    ORGANIZATION CHARTS
Not applicable to this procurement.

[bookmark: _Toc161140856]3.33    RESUMES
Not applicable to this procurement.

[bookmark: _Toc161140857]3.34    EXPERIENCE WITH CONTRACTS OF SIMILAR SIZE AND SCOPE
Not applicable to this procurement.

[bookmark: _Toc161140858]3.35    FINANCIAL CAPABILITY OF THE BIDDER
The Bidder should provide sufficient financial information to enable the State to assess the financial strength and creditworthiness of the Bidder and its ability to undertake and successfully complete the Contract.  In order to provide the State with the ability to evaluate the Bidder’s financial capacity and capability to undertake and successfully complete the Contract, the Bidder should submit the following:
A. For publicly traded companies the Bidder should provide copies or the electronic location of the annual reports filed for the two most recent years; or
B. For privately held companies the Bidder should provide the certified financial statement (audited or reviewed) in accordance with applicable standards by an independent Certified Public Accountant, including a balance sheet, income statement, and statement of cash flow, and all applicable notes for the most recent calendar year or the Bidder’s most recent fiscal year. 

If the information is not supplied with the Quote, the State may still require the Bidder to submit it.  If the Bidder fails to comply with the request within seven (7) business days, the State may deem the Quote non-responsive.

A Bidder may designate specific financial information as not subject to disclosure when the Bidder has a good faith legal/factual basis for such assertion.  The State reserves the right to make the determination to accept the assertion and will so advise the Bidder.

[bookmark: _Toc161140859]3.36    STATE-SUPPLIED PRICE SHEET INSTRUCTIONS
The Bidder must submit its pricing using the State-Supplied Price Sheet accompanying this Bid Solicitation and located on the “Attachments” Tab. 

In order for the State to make sound business judgments regarding products and prices offered in response to this Bid Solicitation, the Bidder must supply, with its Quote, the information requested on the Bid Solicitation’s pricing lines in sufficient detail as to allow the State to determine the firm, fixed Quote pricing and the precise product or service being offered, i.e., with no possible misinterpretation of the price or product/service being offered by the Bidder.  A Bidder’s failure to provide, within its Quote, the information deemed by the State to be essential for product identification or price determination shall result in rejection of that Bidder’s Quote.  Notwithstanding the aforementioned material obligation, in order to support the State's decision-making process, the State may require a Bidder to provide additional information or documentation that has been deemed not to be material to product identification or price determination, in which case, the Bidder shall, within the time limit set forth in the written request, comply with said request.  Each Bidder is required to hold its prices firm through issuance of the Contract.

There are 154 Price Lines, which are itemized as follows:

	Price Line #
	
Description

	Group 1 - Price Lines 1 and 2

	1
	Traffic Signal Indication Parts Replacement Visors – 8 Inch, as per NJDOT Spec. # BME-TS-Visor, Dated April 28, 2010

	2
	Traffic Signal Indication Parts Replacement Visors – 12 Inch, as per NJDOT Spec. # BME-TS-Visor, Dated April 28, 2010

	Individual Price Lines -  Price Lines 3 and 4

	3
	Traffic Signal Indication Parts Scoop Visor – 12 Inch, as per NJDOT Spec. # BME-TS-Scoop Visor, Dated May 31, 2018

	4
	Geometrically Programmed Louver, Plastic 12 Inch Indication as per NJDOT Spec. & NJDOT Sketch # 1 (Attachment #5), Pelco GL-1010 Only - NO SUBSTITUTIONS

	Group 2 - Price Lines 5 and 6

	5
	Traffic Signal Indication Parts Traffic Signal Indication - 8 Inch (Housing Only) as per NJDOT Spec. Dated April 26, 2007 Drawing BME-TS-Head

	6
	Traffic Signal Indication Parts Traffic Signal Indication - 12 Inch (Housing Only) as per NJDOT Spec. No. BME-TS-Head Dated April 26, 2007

	Individual Price Lines -  Price Lines 7 and 8

	7
	Traffic Signal Indication Parts Traffic Signal Indication - Hand/Man (Housing Only) 16" X 18" as per NJDOT Spec. No. BME-TS-Hand/Man Dated May 25, 2010

	8
	Traffic Signal Indication/Parts Visor Screen (Egg Crate) for 16 "X 18" Indication as per NJDOT Spec. No. BME-TS-VSEC Dated May 31, 2018

	Group 3 - Price Lines 9 and 10

	9
	Traffic Signal Indication/Parts 3M-R.A.G. (3 Section – 12 Inch) as per NJDOT Spec. Drawing EB-TS-2

	10
	Traffic Signal Indication/Parts 3M - Arrow  (1 Section) as per NJDOT Spec. Drawing EB-TS-2

	Individual Price Lines -  Price Lines 11 through 30

	11
	Traffic Signal Hangers Brackets Sign Bracket, as per 2007 Standard Electrical Details T-4507 

	12
	Traffic Signal Hangers Brackets Sign Bracket Offset Type, as per 2007 Standard Electrical Details T-4507

	13
	Traffic Signal Hangers Brackets Adapter- Pedestal (Slip Fitter) with Brass Chase Nipple as per 2007 Standard Electrical Details T-0607 and T-0707

	14
	Traffic Signal Hangers Brackets Adapter- Pedestal (Offset Slip Fitter) with Brass Chase Nipple as per NJDOT Sketch #2 (Attachment #5) 

	15
	Traffic Signal Hangers Brackets Band Bracket Assembly- Mid Arm 8-12” Indication 2007 Standard Electrical  Details T-2107, Pelco AS-116-3-29-SS Only - NO SUBSTITUTIONS

	16
	Traffic Signal Hanger Bracket Cable Bracket Assembly – Mid Arm 8-12” Indication 2007 Standard Electrical Details T-2107, Pelco AS-125-3-29-SS Only - NO SUBSTITUTIONS

	17
	Traffic Signal Hanger Bracket Band Bracket Assembly – Mid Arm- 8-12” Indication 2007 Standard Electrical Details T-2107, Pelco AS-103-3-29-SS Only - NO SUBSTITUTIONS

	18
	Traffic Signal Hanger Bracket Cable Bracket Assembly- Mid Arm 8 -12” Indication 2007 Standard Electrical Details T-2107, Pelco AS-151-3-29-SS Only - NO SUBSTITUTIONS

	19
	Traffic Signal Hangers Brackets Clevis- H Mast Arms 2007 Standard Electrical Details T-0407 Universal  Joint 

	20
	Traffic Signal Hangers Brackets Mast Arm Slip Fitter 2007 Standard Electrical Details T-0407 Mast Arm Slip Fitter 

	21
	Traffic Signal Hangers Brackets Universal Joint & Wire Outlet with SS Hardware 2007 Standard Electrical Details T-0407 Universal Joint and Wire Outlet

	22
	Traffic Signal Hangers Brackets Pedestrian Hinge Clamp Assembly for Approx. 7-1/2” Diameter Pole with 12” Standard Nipple 2007 Standard Electrical Details T-0607

	23
	Traffic Signal Hangers Brackets Pedestrian Hinge Clamp Assembly for Approx. 9-1/2” Diameter Pole with 12” Standard Nipple, 2007 Standard Electrical Details T-0607

	24
	Traffic Signal Hangers Brackets Pedestrian Cast Clamp Assembly for Approx. 9-1/2” Diameter Pole with 12” Standard Nipple, 2007 Standard Electrical Details T-0607

	25
	Traffic Signal Hangers Brackets Pedestrian Cast Clamp for Approx. 9-1/2” Diameter Pole with 12” Standard Nipple, 2007 Standard Electrical Details T-0607

	26
	Traffic Signal Hangers Brackets Two-Way Bracket Assembly with T-Bar 2007 Standard Electrical Details T-0507 Hollow Spider for 2-Way Assembly & T-Bar 

	27
	Traffic Signal Hangers Brackets Three-Way Bracket Assembly 2007 Standard Electrical Details T-0507 Hollow Spider for 3-Way Assembly

	28
	Traffic Signal Hangers Brackets Four-Way Bracket Assembly 2007 Standard Electrical Details T-0507 Hollow Spider for 4-Way Assembly

	29
	Traffic Signal Hangers Brackets Pole Clamp Assembly, Hinge Strap Type with 12” Standard Nipple, 2007 Standard Electrical Details T-0607 Pole Clamp Assembly, Hinge Strap Type

	30
	Traffic Signal Hangers Brackets Traffic Signal Safety Chain 2007 Standard Electrical Details T-0307 and T-0907

	Group 4 - Price Lines 31 through 64

	31
	Traffic Signal Poles, Arms, Bases Paint Adder for Poles and Arms Only – Up to and including 23 feet in length 

	32
	Traffic Signal Poles, Arms, Bases Paint Adder for Poles and Arms Only – Over 23 feet in Length

	33
	Traffic Signal Pole & Lighting Pole Bases Paint Adder for Bases Only

	34
	Traffic Signal Hangers Brackets TB-20 Base 2007 Standard Electrical Details T-0207

	35
	Traffic Signal Hangers Brackets HHB Base 2007 Standard Electrical Details T-1507

	36
	Traffic Signal Hangers Brackets K Base 2007 Standard Electrical Details T-1007

	37
	Traffic Signal Hangers Brackets Traffic Signal Pole Type T-2007 Standard Electrical Details T-0107

	38
	Traffic Signal Hangers Brackets Traffic Signal Pole Type C 2007 Standard Electrical Details T-0807

	39
	Traffic Signal Hangers Brackets Traffic Signal Pole Type K 2007 Standard Electrical Details T -1007

	40
	Traffic Signal Hangers Brackets Pedestal Pole – 8 Foot 2007 Standard Electrical Details T-0707

	41
	Traffic Signal Hangers Brackets Pedestal Pole – 12 Foot 2007 Standard Electrical Details T-0707

	42
	Traffic Signal Hangers Brackets Traffic Signal Standard, Type KE 2007 Standard Electrical Details T -1007

	43
	Traffic Signal Pole, Type KE Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch #3 (Attachment #5)

	44
	Traffic Signal Poles, Arms, Bases Traffic Signal Pole Type K - Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch #4 (Attachment #5)

	45
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – Trombone 15 ft. as per NJDOT Drawing T-1207

	46
		Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – Trombone 20 ft. as per NJDOT Drawing T-1207




	47
		Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm –15 ft. as per NJDOT Drawing T-0307




	48
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 20 ft. as per NJDOT Drawing T-0307

	49
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 25 ft. as per NJDOT Drawing T-0307

	50
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 15 ft. Type K as per NJDOT Drawing T-0907

	51
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 20 ft. – Type K as per NJDOT Drawing T-0907

	52
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 25 ft. – Type K as per NJDOT Drawing T-0907

	53
	Traffic Signal Poles, Arms, Bases Traffic Signal Standard Type T Pole Cap as per NJDOT Drawing T-0107

	54
	Traffic Signal Poles, Arms, Bases Traffic Signal Standard Type K Pole Cap as per NJDOT Drawing T-1007 Detail C

	55
	Paint Adder Poles, Arms, Lighting Poles, Arms

	56
	Lighting  Poles, Arms, Bases Lighting Pole,  Type L as per NJDOT Spec. Drawing P-0189

	57
	Lighting Poles, Arms, Bases Lighting  Pole, Type L-40 as per NJDOT Spec. Drawing P-0289

	58
	Lighting Poles, Arms, Bases Lighting Arm, 8 Foot as per NJDOT Spec. Drawing P-0389

	59
	Lighting Poles, Arms, Bases Lighting Arm, 15 Foot as per NJDOT Spec. Drawing P-0389

	60
	Lighting Poles, Arms, Bases Transformer Base (Lighting) as per NJDOT Spec. Drawing L-2107

	61
	Lighting Poles, Arms, Bases, Lighting Pole, 22 Foot Bridge Mounted Pole – Flagpoles Inc. #RTA8M22AABXV-HH, Arm In Line with Hand Hole 12 inches from Bottom with Vibration Dampener, Flagpoles #RTA8M22AABXV-HH  Only - NO SUBSTITUTIONS

	62
	Lighting Poles, Arms, Bases, Lighting Pole, 37 Foot Bridge Mounted Pole - Flagpoles Inc. #RTA8X37AABXV-HH, Arm In Line with Hand Hole 12 inches From Bottom with Vibration Dampener, Flagpoles #RTAX837AABXV-HH Only - NO SUBSTITUTIONS

	63
	Lighting Poles, Arms, Bases Lighting Arm Assembly as per NJDOT Sketch #5 (Attachment #5)

	64
	Lighting Poles, Arm, Bases Mounting Adapter for Offset Luminaire as per NJDOT Drawing L -1807

	Group 5 - Price Lines 65 through 78

	65
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Standard Type S (Includes Anchorage) with Alternate Pole Top as per Bid Solicitation Specifications and NJDOT Detail T-1107 & T-4307 and Reference Sketch #3 and Sketch #4 (Attachment #5)

	66
		Steel Traffic Signal Poles and Arms Steel Traffic Signal Standard Type SC (Includes Anchorage) with Alternate 
Pole Top as per Bid Solicitation Specifications and NJDOT Detail T-1107 & T-4307 and Reference 
Sketch #3 and Sketch #4 (Attachment #5)




	67
	Traffic Signal Poles, Arms, Bases Steel Traffic Signal Arm - 20 ft. as per NJDOT Drawing T-1307

	68
	Traffic Signal Poles, Arms, Bases Steel Traffic Signal Arm - 25 ft. as per NJDOT Drawing T-1307

	69
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Arm - 30 ft. as per NJDOT Drawing T-1307

	70
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Arm- 35 ft. as per NJDOT Drawing T-1307

	71
	Steel Traffic Signal Poles and Arms, Bases Steel Traffic Signal Arm- 40 ft. as per NJDOT Drawing T-1307

	72
	Steel Traffic Signal Poles and  Arms, Bases Steel Traffic Signal Arm- 45 ft. as per NJDOT Drawing T-1307

	73
	Steel Traffic Signal Poles and Arms, Bases Steel Traffic Signal Arm- 50 ft. as per NJDOT Drawing T-1307

	74
	Steel Traffic Signal Poles and Arms, Steel Traffic Signal Standard, Type SC Lighting Arm - 15 ft., as per NJDOT Drawing T -1307

	75
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Standard, Type SC Lighting Arm - 20 ft., as per NJDOT  Drawing T-1307

	76
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Anchorages as per NJDOT Drawing T-4307

	77
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Type S - Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch # 4

	78
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Type SC -Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch # 4

	Group 6 - Price Lines 79 through 88

	79
	Paint Adder Cabinet - Up to and Including 23 Feet in Length, as per Bid Solicitation Sections 4.7 and 4.23 for Cabinets and Cabinet Hardware

	80
	Paint Adder Cabinet - Over  23 Feet in Length, as Per Bid Solicitation Sections 4.7 and 4.23 Cabinets and Cabinet Hardware 

	81
	Cabinets and Cabinet Hardware Meter Cabinet, Type T As Per NJDOT Spec. Drawing P -0489, and NJDOT Drawing T-4307

	82
	Cabinets and Cabinet Hardware Meter Cabinet Type T (Sheet Metal), as per NJDOT Spec. Drawing T -3507

	83
	Cabinets and Cabinet Hardware Meter Cabinet, Fabricated Typed (53 Inch), as per NJDOT Sketch #11 (Attachment #5)

	84
	Cabinets and Cabinet Hardware Meter Cabinet Type M (Sheet Metal), as per NJDOT Spec. Drawing L -1407

	85
	Cabinets and Cabinet Hardware Cabinet Type P, as per NJDOT Sketch #6 (Attachment #5)

	86
	Cabinets and Cabinet Hardware Cabinet Type P Split Skirt, as per NJDOT Sketch #7 (Attachment #5)

	87
		Cabinets and Cabinet Hardware Cabinet, Type P Skirt, as per NJDOT Sketch #7 (Attachment #5)




	88
		Cabinets and Cabinet Hardware Meter Cabinet Type M  - Lock & Keys, as per NJDOT Spec. Drawing L -1407




	Individual Price Lines - Price Lines 89 and 90

	89
	Cabinets and Cabinet Hardware Meter Cabinet, Composite Carlon Part #C2420A4 Only - NO SUBSTITUTIONS

	90
	Cabinets and Cabinet Hardware Controller Cabinet, Lock & Keys S591, as per NJDOT Sketch #8  (Attachment #5), CCL Products A55481RS: Right Hand, Dead Bolt Only - NO SUBSTITUTIONS

	Group 7 - Price Lines 91 through 95

	91
	Signs/ Sign Brackets Sign – Red Signal Ahead – LED, as per NJDOT Spec. Drawing T -1407

	92
	Signs/Sign Brackets – Blankout Sign LED “No Left Turn”, as per NJDOT Drawing T-1407 & Sketch #10 (Attachment #5)

	93
	Signs/Sign Brackets – Blankout Sign LED “No Right Turn”, as per NJDOT Drawing T-1407 & Sketch #10 (Attachment #5)

	94
	Signs/Sign Brackets – Blankout Sign LED “No Turn On Red” 2007 Standard Electrical Detail T -1407, as per NJDOT Drawing T-1407,BME – LED-NTBLO Dated 5/31/2018 & NJDOT Sketch #10 (Attachment #5)

	95
	Signs/Sign Brackets – Blankout Sign LED (Message To Be Determined When Ordering) 2007 Standard Electrical Detail T -1407, as per NJDOT Drawing T-1407, BME  LED-NTBLO Dated 5/31/2018 & Sketch #10 (Attachment #5)

	Individual Price Lines- Price Lines 96 through 100

	96
	Signal Control Devices, Detector (Microwave), as per NJDOT Spec. Drawing Model TC-26B

	97
	Signal Control Devices, Detector (Microwave), as per NJDOT Spec. Drawing Model TC-30

	98
	Signal Control Devices, Loop Detector – 4 Channel, as per NJDOT Spec. EB-LD-3

	99
	Signal Control Devices, Detector Card, as per NJDOT Spec. EB-LD-CARD

	100
	Signal Control Devices, Uninterruptible Power System- 850 Watts, as per NJDOT Spec. #BME-UPS-1, Dated 9/22/2014

	Group 8 - Price Lines 101 and 102

	101
	Miscellaneous Signal Products Devices, Wireless Transceiver System-2, Including All Mounting Hardware, Antennas, Connectors, Cables for a Complete System, as per NJDOT Spec. BME-WCCS, Dated 5/24/10

	102
	Miscellaneous Signal Products Devices, Wireless Transceiver System-3, Including All Mounting Hardware, Antennas, Connectors, Cables for a Complete System, as per NJDOT Spec. BME-WCCS, Dated 5/24/10

	Group 9 – Price Lines 103 and 104

	103
	Miscellaneous Signal Products Devices, Backplate – 8” Signal Head, as per NJDOT Drawing T-1807

	104
	Miscellaneous Signal Products Devices, Backplate – 12” Signal Head, as per NJDOT Drawing T-1807

	Group 10 - Price Lines 105 through 108

	105
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base TB-20, as per NJDOT Drawing T-0207

	106
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base K, as per NJDOT Drawing T-0707

	107
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base TB-30, as per NJDOT Drawing L-1507

	108
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base TB-17, as per NJDOT Drawing L-2107

	Group 11 - Price Lines 109 through 111

	109 
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Econolite 5 Inch Border Aluminum, Black Non-Louvered 3 Section with 3 Inch 3M Tape Border - Econolite P43-01 Only - NO SUBSTITUTIONS

	110
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Econolite 5 Inch Border, Aluminum, Black Non-Louvered 4 Section with 3 Inch 3M Tape Border - Econolite P44-01 Only - NO SUBSTITUTIONS

	111
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Econolite 5 Inch Border, Aluminum, Black Non-Louvered 5 Section with 3 Inch 3M Tape Border - Econolite P45-01 Only - NO SUBSTITUTIONS

	Group 12 - Price Lines 112 through 114

	112
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, McCain Aluminum Black Non-Louvered 3 Section with 3 Inch 3M Tape Border - McCain HP Only - NO SUBSTITUTIONS

	113
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, McCain Aluminum Black Non-Louvered 4 Section with 3 Inch 3M Tape Border - McCain HP Only - NO SUBSTITUTIONS

	114
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Mccain Aluminum Black Non-Louvered 5 Section with 3 Inch 3M Tape Border - McCain HP Only - NO SUBSTITUTIONS

	Individual Price Lines – Price Lines 115 and 116

	115
	Miscellaneous Signal Products Devices, GPS Time Reference - Garmin Only - NO SUBSTITUTIONS

	116
	Miscellaneous Signal Products Devices, GPS Time Reference - Eltec Time Sync 1-GPS Only - NO SUBSTITUTIONS

	Group 13 - Price Lines 117 through 121

	117
	Traffic Signals and Equipment Traffic Signal Cable 2/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	118
	Traffic Signals and Equipment Traffic Signal Cable 5/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	119
	 Traffic Signals and Equipment Traffic Signal Cable 7/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	120
	Traffic Signals and Equipment Traffic Signal Cable 10/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	121
	Traffic Signals and Equipment Traffic Signal Cable 14/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	Group 14 - Price Lines 122 and 123

	122
	Hand/Man Pedestrian Signal Head, as per NJDOT Spec. BMEO-LED-H/M-PSH- Dated: 09/16/2014 and Bid Solicitation Specifications

	123
	Hand/Man Pedestrian Signal Head, as per NJDOT Spec. BMEO-LED-H/M-PSM- Dated: 09/16/2014 and Bid Solicitation Specifications

	  Group 15 - Price Lines 124 through 126

	124
	Red, Amber, Green LED Module for Optically Programmed Traffic Signal Red Module, as per NJDOT Spec. BMEO-OP-RAG Dated 01/16/2014 and Bid Solicitation Specifications

	125
	Red, Amber, Green LED Module for Optically Programmed Traffic Signal Amber Module, as per NJDOT Spec. BMEO-OP-RAG Dated 01/16/2014 and Bid Solicitation Specifications

	126
	Red, Amber, Green LED Module for Optically Programmed Traffic Signal Green Module, as per NJDOT Spec. BMEO-OP-RAG Dated 01/16/2014 and Bid Solicitation Specifications

	Individual Price Lines – Price Lines 127 and 128

	127
	Indication LED Solar Beacon Assembly 12” Amber, as per NJDOT Spec. BMEO-LED-SFB Dated 09/16/2014 and Bid Solicitation Specifications

	128
	Adjustable Face Vehicle Traffic Control Aluminum Signal Head (Housing Only 3-12” Sections), as per NJDOT Spec. BMEO-TSH-AL, Dated 1/16/2014 and the Bid Solicitation Specifications

	Individual Price Lines - Price Lines 129 through 139

	129
	Lighting Poles Arms, Bases Black Lighting Arm Assembly as per NJDOT Sketch #12 (Attachment #5)

	130
	Generator Auxiliary Cabinet (GAC) as per Bose GAC-Alpha Dated January 24, 2024, Alpha Only - NO SUBSTITUTIONS

	131
	Generator Auxiliary Cabinet (GAC), as per Bose-GAC-Other Dated January 24, 2024

	132
	Audible Push Button System 8 APS and Control Unit – Polara INS23TNO-Y WITH iCCU-S2 Only - NO SUBSTITUTIONS

	133
	Audible Push Button System 8 APS and Control Unit – Campbell WiAAPS APC 501-0910C - NO SUBSTITUTIONS

	134
	Pedestrian Pole Assembly, as per NJDOT Sketch #13 (Attachment #5) Only - NO SUBSTITUTIONS

	135
	Pedestrian Pole Assembly, as per NJDOT Sketch #13 (Attachment #5)

	136
	Traffic Signal Pole Assembly, as per NJDOT Sketch #14 (Attachment #5) Only - NO SUBSTITUTIONS

	137
	Traffic Signal Pole Assembly, as per NJDOT Sketch #14 (Attachment #5)

	138
	Econolite Cobalt Signal Controller - NO SUBSTITUTIONS

	139
	Trafficware Commander Signal Controller - NO SUBSTITUTIONS

	Individual Price Lines – Percentage Discount or Markup from the Brand Manufacturer’s Price List/Catalog Pricing - Price Lines 140 through 154

	140
	Polara Brand Only – Price List - NO SUBSTITUTIONS

	141
	General Fasteners (Any Brand) – Price List 

	142
	Campbell Brand Only – Price List - NO SUBSTITUTIONS

	143
	Econolite Signal Controller Brand Only – Price List - NO SUBSTITUTIONS

	144
	Trafficware Signal Controller Brand Only – Price List - NO SUBSTITUTIONS

	145
	Gridsmart Brand Only – Price List - NO SUBSTITUTIONS

	146
	Miovision Brand Only – Price List - NO SUBSTITUTIONS

	147
	Wavetronix Brand Only – Price List - NO SUBSTITUTIONS

	148
	2-Way Assemblies Components - Pelco Inc. Brand Only - Price List  - NO SUBSTITUTIONS

	149
	Audible Push Button System Components – Polara Brand Only – Price List - NO SUBSTITUTIONS

	150
	Audible Push Button System Components - Campbell Brand Only – Price List - NO SUBSTITUTIONS

	151
	Aeroflex Back Plate - Pelco Inc. Brand Only  - Price List - NO SUBSTITUTIONS

	152
	Alpha Brand Only – Price List - NO SUBSTITUTIONS

	153
	1-Way Assemblies Components - Pelco Inc. Brand Only – Price List - NO SUBSTITUTIONS

	154
	Beacon-4-Life Brand Only – Price List - NO SUBSTITUTIONS



The State intends to make awards as follows:

For Groups 1 through 15:

For Groups 1 through 15 the State intends to make one (1) Contract award per Group.

Bidders must bid on all price lines contained within the Group.  If a Bidder does not bid on all price lines within the Group, its Quote will be considered non-responsive for that Group.

If a brand/product bid on a price line within the group is deemed non-responsive, the entire group that price line item is part of will be deemed non-responsive, as these price lines were grouped to create a single award, with the intent that all price lines in the group will be awarded. 

A Bidder is not required to bid on all Groups on the State-Supplied Price Sheet in order to be considered responsive.  

Price line items are grouped for Quote evaluation purposes only.  Upon Contract award, Using Agencies will be able to order any price lines within the Groups individually.

For Individual Price Lines – Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139:  

The Bid Solicitation contains Individual Price Lines, identified as Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139 on the State-Supplied Price Sheet.  A Bidder may bid on one, some or all Individual Price Lines (Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139).  A Bidder is not required to bid on all Individual Price Lines on the State-Supplied Price Sheet in order to be considered responsive.

For each individual price line, the State intends to make one (1) Contract award.

For Individual Price Lines – Price Lines 140 through 154:  

A Bidder may bid on one, some or all Individual Price Lines for Price Lines 140 through 154.  A Bidder is not required to bid on all Individual Price Lines on the State-Supplied Price Sheet in order to be considered responsive.

For individual price lines 140 through 154, the State intends to make a Contract award to all responsive Bidders.

Important - General: 

In certain instances, the brand or manufacturer name and/or product name or model number fields within the Groups and/or individual price lines are populated to represent specific makes and models of items required by the Using Agencies.  In these instances, Bidders shall not substitute any brand or manufacturer names and/or product name or model numbers contained within each price line.

For Price Lines 140 through 154, Bidders should refer to Bid Solicitation Section 3.24 regarding the submission of catalogs/price lists.

For individual price lines that are not populated with specific manufacturer/brand names and product names or model numbers, a Bidder may bid more than one manufacturer/brand name and product name or model number for each price line.  Bidders offering more than manufacturer/brand name and product name or model number for each price line should submit a separate State-Supplied Price Sheet for each manufacturer/brand name and product name or model number offered.  In the alternative, Bidders may add tabs to the bottom of the State-Supplied Price Sheet for additional manufacturer/brand names and product names or model numbers for each price line bid (by copying the text and information from the original Price Sheet).  The Bidder must follow all instructions and provide all required information contained within this Bid Solicitation Section for each additional brand offered.  

Instructions:

Step 1 - The Bidder should enter the Bidder’s name in the “Bidder’s Name” field located at the top of the State Price Sheet.

Step 2 – The Bidder should enter the cash discount for expedited payments into the “Cash Discount for Expedited Payment” field on State-Supplied Price Sheet.  If the Bidder leaves the “Cash Discount for Expedited Payment” field blank, it shall mean that the Bidder is not offering a cash discount.

Step 3 – For the price lines that comprise Groups 1 through 15 and for Individual Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139, the Bidder shall insert a firm, fixed price in U.S. dollars in the “Unit Price” field on the State-Supplied Price Sheet.  The Unit price bid must include any freight/shipping/handling costs.

For Groups 1 through 15, Bidders must bid on all price lines contained within each Group in order to be considered a responsive Bidder for the Group.  If a Bidder does not bid on all price lines within the Group, its Quote will be considered non-responsive for the Group.  If a Bidder leaves the “Unit Price” field blank, it shall be considered that the Bidder provided no Quote for that price line item.  
A Bidder is not required to bid on all Groups on the State-Supplied Price Sheet in order to be considered responsive. 

Bidders may bid on all, some, or none of the individual price line items.  A Bidder is not required to bid on all individual price lines on the State-Supplied Price Sheet in order to be considered responsive.

Unit Prices may be offered on the State Supplied Price Sheet up to two (2) decimal places to the right of the decimal point.  Price sheet formatting will automatically round Unit Prices containing more than two (2) decimal places to the right of the decimal point so as not to exceed this limit.

Step 4 – For Price Lines  1 through 3, 5 through 14, 19 through 60, 63 through 88, 91 through 108, 117 through 129, 131, 134 through 137, and 141:  The Bidder shall enter the brand or manufacturer in the “Manufacturer/Brand Name” field.  

For Price Lines 4, 15, 16, 17, 18, 61, 62, 89, 90, 109, 110, 111, 112, 113, 114, 115, 116, 130, 132, 133, 138 and 139, no substitute manufacturer/brand names are permitted for these Price Lines.  These Price Lines are pre-populated with specific brand/manufacturer names in the “Manufacturer/Brand” field on the State-Supplied Price Sheet.  Any attempt by a Bidder to alter these brand/manufacturer names on the State-Supplied Price Sheet will render the Bidders Quote non-responsive for that price line item, and, if applicable, any Group that price line item is part of.

Step 5 - For Price Lines 1 through 3, 5 through 14, 19 through 60, 63 through 88, 91 through 108, 115, 117 through 129, 130, 131 and 134 through 137:  The Bidder shall enter the product name or product model number in the “Product Name or Model Number” field.  

For Price Lines 4, 15, 16, 17, 18, 61, 62, 89, 90, 109, 110, 111, 112, 113, 114, 116, 132, 133, 138 and 139, no substitute product names or model numbers are permitted for these Price Lines.  These Price Lines are a pre-populated with specific product names or model numbers in the “Product Name or Model Number” field on the State-Supplied Price Sheet.  Any attempt by a Bidder to alter these product names or model numbers on the State-Supplied Price Sheet will render the Bidders Quote non-responsive for that price line item, and, if applicable, any Group that price line item is part of.

Step 6 – For Individual Price Lines 140 through 154, the Bidder shall insert a firm, fixed percentage (%) discount or mark-up from the product catalog/price list, by entering the percentage discount or mark-up bid in the "Percentage (%) Discount (-) or Mark-Up (+)” field on the price line on the State-Supplied Price Sheet.  A Bidder's entry in the "Percentage (%) Discount (-) or Mark-Up (+)” field shall be considered a percentage (%).  For example, an entry of "50" shall be considered "50%" and that of "0.50" shall be considered "0.50%".

The State will accept up to two (2) decimal places to the right of the decimal point.  Percentages may be offered on the State-Supplied Price Sheet up to two (2) decimal places to the right of the decimal point.  Price Sheet formatting will automatically round percentages containing more than two (2) decimal places to the right of the decimal point so as not to exceed this limit.

A Bidder’s entry in the “Percentage (%) Discount (-) or Markup (+)” field shall include a plus (+) sign for markup or minus (-) sign for discount.  If a Vendor “Bidder” does not include a plus (+) sign for markup or minus (-) sign for discount, the State will consider the percentage offered as a discount. 

If a Bidder leaves the "Percentage (%) Discount (-) or Markup (+)” field blank on the price line, it shall be considered that the Bidder provided no Quote for the price line item.  

A series or a range of discounts/markups or fixed prices (firm dollar amount) on the price line shall not be acceptable and shall result in rejection of the Quote for that price line only. 

If a Bidder is offering its pricing at the same pricing listed on the pre-printed catalog/price list, the Bidder should insert 0% in the “Percentage (%) Discount (-) or Markup (+)” field on the State-Supplied Price Sheet.

For Price Lines 140, 142, 143, 144, 145, 146, 147, 148, 149, 150, 151, 152, 153 and 154:  These Price Lines are a pre-populated with specific manufacturer/brand names in the “Manufacturer/Brand” field on the State-Supplied Price Sheet.  Any attempt by a Bidder to alter these manufacturer/brand names on the State-Supplied Price Sheet will render the Bidders Quote non-responsive for that price line item. 

For Price Line 141 (General Fasteners):  The Bidder shall enter the brand or manufacturer in the “Manufacturer/Brand Name” field.  

Bidders may bid any manufacturer/brand of general fasteners that can be used in conjunction with the types of equipment specified in this Bid Solicitation.

Bidders may bid multiple brands for this price line.  Bidders offering more than one brand for this price line should submit a separate State-Supplied Price Sheet for each brand offered.  In the alternative, Bidders may add tabs to the bottom of the State-Supplied Price Sheet for additional brands bid for Price Line 141 (by copying the text and information from the original Price Sheet).  The Bidder must follow all instructions and provide all required information contained within this Bid Solicitation Section for each additional brand offered.  Bidders may bid (list) all brands bid in the fields provided for price line 141, provided that the information is clear and concise, so that the State can easily determine which percentage discount or markup coincides with each brand bid.

Please be advised that Steps 3, 4, 5, and 6 are required fields that must be completed on the State-Supplied Price Sheet.  A Bidder’s failure to complete these fields on the State-Supplied Price Sheet shall render the Bidder’s Quote non-responsive.

Step 7 – The Bidder should enter the days required to make delivery after receipt of an order (ARO) into the “Delivery Days After Receipt of Order (ARO)” field of the State-Supplied Price Sheet for each price line item.  If the “Delivery Days After Receipt of Order (ARO)” field is left blank, then the delivery days shall default to the delivery days set forth in Section 5.6.

Where the State-Supplied Price Sheet includes an estimated quantity column, Bidders are advised that estimated quantities may vary throughout the Contract term resulting from this Bid Solicitation.  There is no guaranteed minimum or maximum volume for these price lines. 

Any price changes including hand written revisions or "white-outs" must be initialed.  Failure to initial price changes shall preclude a Contract award from being made to the Bidder pursuant to N.J.A.C. 17:12-2.2(a)(8).

[bookmark: _Toc161140860]3.36.1    DELIVERY TIME AND COSTS
Unless otherwise noted elsewhere in the Bid Solicitation or State Price sheet, all delivery times are as noted in Bid Solicitation Section 5.6 Delivery Time and Costs.  Bidder may submit alternate delivery days on the State Price Sheet.  Alternate delivery times shall not exceed the delivery days noted in Bid Solicitation Section 5.6.  Quotes that exceed the delivery days of Bid Solicitation Section 5.6 may be deemed non-responsive. 

When there is a discrepancy between the delivery days listed in the General Tab in the Quote in NJSTART and the State Price Sheet, the State Price Sheet delivery days shall govern.  

[bookmark: _Toc161140861]3.36.2    CASH DISCOUNTS
The Bidder is encouraged to offer cash discounts based on expedited payment by the State.  The State will make efforts to take advantage of discounts, but discounts will not be considered in determining the price rankings of Quotes.  Should the Bidder choose to offer cash discounts, the following shall apply:
A. Discount periods shall be calculated starting from the next business day after the Using Agency has accepted the goods or services, received a properly signed and executed invoice and, when required, a properly executed performance security, whichever is latest; and
B. The date on the check issued by the State in payment of that invoice shall be deemed the date of the State's response to that invoice.

[bookmark: _Toc161140862]3.36.3    VOLUME DISCOUNTS
Not applicable to this procurement.



[bookmark: _Toc161140863]3.36.4     USE OF “NO BID” ON THE STATE-SUPPLIED PRICE SHEET
All price lines must be filled out in accordance with the instructions above.  If the Bidder is not submitting a price for an item on a price line, the Bidder must indicate “No Bid” on the State-Supplied Price Sheet accompanying this Bid Solicitation.  The use of any other identifier may result in the Bidder’s Quote being deemed non-responsive.

[bookmark: _Toc161140864]3.37    ORAL PRESENTATIONS
Not applicable to this procurement.



[bookmark: _Toc161140865]SCOPE OF WORK
[bookmark: _Toc400531507][bookmark: _Toc428533978][bookmark: _Toc32310703]NJDOT’s Specification numbers are referenced in this Bid Solicitation and on the price lines on the State-Supplied Price Sheet, as applicable. See Electrical Material Specifications (English), Traffic Engineering, Engineering (state.nj.us) 

The intent and purpose of the NJDOT specifications are to describe the minimum acceptable requirements for items requested under this Bid Solicitation.

[bookmark: _Toc529958827][bookmark: _Toc51168001][bookmark: _Toc161140866]4.1    TECHNICAL SPECIFICATIONS
The following categories of traffic component parts are covered under this Bid Solicitation:

	SECTIONS
	CATEGORIES

	Section A
	Traffic signal indications/parts

	Section B
	Traffic signal hangers/brackets

	Section C
	Traffic signal poles, arms, bases

	Section D
	Lighting poles, arms, bases

	Section E
	Steel traffic signal poles and arms

	Section F
	Cabinets and cabinet hardware

	Section G
	Signs/sign brackets

	Section H
	Signal control devices

	Section I
	Miscellaneous signal products/devices

	Section J
	Traffic Signal Cable



[bookmark: _Toc161140867]4.2    SECTION A - TRAFFIC SIGNAL INDICATIONS PARTS

	Descriptions

	Replacement Visor 8 inch
	NJ Specification No. BME-TS-VISOR
Dated April 28, 2010
Delivery Schedule “A” – 16 weeks

	Replacement Visor 12 inch
	NJ Specification No. BME-TS-VISOR
Dated April 28, 2010
Delivery Schedule “A” – 16 weeks

	Scoop Visor
	BME-TS-SCOOP VISOR
Dated May 31, 2018
Delivery Schedule “A” – 16 weeks

	Geometrically Programmed Louver, Plastic 12” Indication
	NJDOT SKETCH #1
Delivery Schedule “A” – 16 weeks

	Traffic Signal Indication 8 inch (Housing Only)
	NJ Specification No. BME-TS-HEAD
Dated April 26, 2007
Delivery Schedule “A” – 16 weeks

	Traffic Signal Indication 12 inch (Housing Only)
	NJ Specification No. BME-TS-HEAD
Dated April 26, 2007
Delivery Schedule “A” – 16 weeks

	Traffic Signal Indication Hand/Man (Housing Only) 16” x 18”
	NJ Specification No. BME-TS-HAND/MAN
Dated April 26, 2007
Delivery Schedule “A” – 16 weeks

	Visor Screen (Egg Crate for 16” x 18” Indication
	NJ Specification No. BME-TS-VSEC
Dated May 25, 2010
Delivery Schedule “A” – 16 weeks

	3M R.A.G (3 section – 12”)
	NJDOT Spec. Drawing EB-TS-2 http://www.state.nj.us/transportation/eng/elec/TSS/english/ Delivery Schedule “A” – 16 weeks

	3M – Arrow (1 section)
	NJDOT Spec. Drawing EB-TS-2 http://www.state.nj.us/transportation/eng/elec/TSS/english/ Delivery Schedule “A” – 16 weeks



[bookmark: _Toc161140868]4.3    SECTION B - TRAFFIC SIGNAL HANGERS BRACKETS

	Descriptions

	Sign Bracket
	2007 Standard Electrical Details T-4507
Delivery Schedule “A” – 16 weeks

	Sign Bracket Offset Type
	2007 Standard Electrical Details T-4507
Delivery Schedule “A” – 16 weeks

	Adapter-Pedestal (Slip fitter) with Brass Chase Nipple
	2007 Standard Electrical Details T-0607 and T-0707
Delivery Schedule “A” – 16 weeks

	Adapter-Pedestal (Offset Slip fitter) with Brass Chase Nipple
	NJDOT SKETCH #2
Delivery Schedule “A” – 16 weeks

	Band Bracket Assembly – Midarm 8” – 12” Indication
	2007 Standard Electrical Details T-2107
Delivery Schedule “A” – 16 weeks

	Cable Bracket Assembly– Midarm  8” – 12” Indication
	2007 Standard Electrical Details T-2107
Delivery Schedule “A” – 16 weeks

	Clevis – H Mast Arms
	2007 Standard Electrical Details T-0407
Universal Joint
Delivery Schedule “A” – 16 weeks

	Mast Arm Slip fitter
	2007 Standard Electrical Details T-0407
Mast Arm Slip fitter
Delivery Schedule “A” – 16 weeks

	Universal Joint and Wire Outlet with S/S Hardware
	2007 Standard Electrical Details T-0407
Universal Joint and Wire Outlet
Delivery Schedule “A” – 16 weeks

	Pedestrian Clamp Type Assembly for Approx. 7-1/2” Dia. Pole – 12” STD Nipple
	2007 Standard Electrical Details T-0607
Delivery Schedule “A” – 16 weeks

	Pedestrian Clamp Type Assembly for Approx. 9-1/2” Dia. Pole – 12” STD Nipple
	2007 Standard Electrical Details T-0607
Delivery Schedule “A” – 16 weeks

	Two-way bracket Assembly with T-Bar
	2007 Standard Electrical Details T-0507
Hollow Spider for 2-way Assembly and T-Bar
Delivery Schedule “A” – 4 weeks

	Three-way bracket Assembly
	2007 Standard Electrical Details T-0507
Hollow Spider for 3-way Assembly
Delivery Schedule “A” – 16 weeks

	Four-way bracket Assembly
	2007 Standard Electrical Details T-0507
Hollow Spider for 4-way Assembly
Delivery Schedule “A” – 16 weeks

	Pole Clamp Assembly, Hinge Strap Type – 12” STD Nipple
	2007 Standard Electrical Details T-0607
Pole Clamp Assembly Hinge Strap Type
Delivery Schedule “A” – 16 weeks

	Traffic Signal Safety Chain
	2007 Standard Electrical Details T-0307 and T-0907
Delivery Schedule “A” – 16 weeks




[bookmark: _Toc161140869]4.4    SECTION C - TRAFIC SIGNAL POLES ARMS, BASES

	Descriptions

	Paint Adder Poles, Arms, Bases
	Traffic Signal Poles, Arms, Bases

	TB-20 Base
	2007 Standard Electrical Details T-0207
Delivery Schedule “B” – 24 weeks

	HHB Base
	2007 Standard Electrical Details L-1507
Delivery Schedule “B” – 24 weeks

	K Base
	2007 Standard Electrical Details T-1007
Delivery Schedule “B” – 24 weeks

	Traffic Signal Pole Type T
	2007 Standard Electrical Details T-0107
Delivery Schedule “B” – 24 weeks

	Traffic Signal Pole Type C
	2007 Standard Electrical Details T-0807
Delivery Schedule “B” – 24 weeks

	Traffic Signal Pole Type K
	2007 Standard Electrical Details T-1007
Delivery Schedule “B” – 24 weeks

	Pedestal Pole 8 Foot
	2007 Standard Electrical Details T-0707
Delivery Schedule “B” – 24 weeks

	Pedestal Pole 12 Foot
	2007 Standard Electrical Details T-0707
Delivery Schedule “B” – 24 weeks

	Traffic Signal Standard Type KE
	2007 Standard Electrical Details T-1007
Delivery Schedule “B” – 24 weeks

	Traffic Signal Standard Type KE Mounting Adapter for Mongoose Luminaire
	DOT Sketch # 3
Delivery Schedule “B” – 24 weeks

	Traffic Signal Standard Type K Mounting Adapter for Mongoose Luminaire
	DOT Sketch # 4
Delivery Schedule “B” – 24 weeks

	Traffic Signal Mast Arm 15 Foot Trombone
	2007 Standard Electrical Details T-1207
Delivery Schedule “B” – 24 weeks

	Traffic Signal Mast Arm 20 Foot Trombone
	2007 Standard Electrical Details T-1207
Delivery Schedule “B” – 24 weeks

	Traffic Signal Mast Arm 15 Foot
	2007 Standard Electrical Details T-0307
Delivery Schedule “B” – 24 weeks

	Traffic Signal Mast Arm 20 Foot
	2007 Standard Electrical Details T-0307
Delivery Schedule “B” – 24 weeks

	Traffic Signal Mast Arm 25 Foot
	2007 Standard Electrical Details T-0307
Delivery Schedule “B” – 24 weeks

	Traffic Signal Mast Arm 15 Foot Type K
	2007 Standard Electrical Details T-0907
Delivery Schedule “B” – 24 weeks

	Traffic Signal Mast Arm 20 Foot Type K
	2007 Standard Electrical Details T-0907
Delivery Schedule “B” – 24 weeks

	Traffic Signal Mast Arm 25 Foot Type K
	2007 Standard Electrical Details T-0907
Delivery Schedule “B” – 24 weeks

	Traffic Signal Standard Type T Pole Cap
	2007 Standard Electrical Details T-0107
Detail “B”
Delivery Schedule “B” – 24 weeks

	Traffic Signal Standard Type K Pole Cap
	2007 Standard Electrical Details T-1007
Detail “C”
Delivery Schedule “B” – 24 weeks



[bookmark: _Toc161140870]4.5    SECTION D - LIGHTING POLES, ARMS, BASES

	Descriptions

	Paint Adder Poles, Arms, Bases
	Lighting Poles, Arms, Bases
Delivery Schedule “C” – 48 weeks

	Lighting Pole Type L
	DOT Spec Drawing P-0189
Delivery Schedule “B” – 24 weeks

	Lighting Pole Type L 40
	DOT Spec Drawing P-0289
Delivery Schedule “B” – 24 weeks

	Lighting Arm 8 Foot
	DOT Spec Drawing P-0389
Delivery Schedule “B” – 24 weeks

	Lighting Arm 15 Foot
	DOT Spec Drawing P-0389
Delivery Schedule “B” – 24 weeks

	Transformer Base Lighting
	2007 Standard Electrical Details T-2107
Delivery Schedule “B” – 24 weeks

	Lighting Arm Assembly
	DOT Sketch # 5
Delivery Schedule “B” – 24 weeks

	Mounting Adapter for Offset Luminaire
	2007 Standard Electrical Details L-1807
Delivery Schedule “B” – 24 weeks



[bookmark: _Toc161140871]4.6    SECTION E - STEEL TRAFFIC SIGNAL POLES AND ARMS

	Descriptions

	Steel Traffic Signal Standard (includes anchorage)
	2007 Standard Electrical Details T-1107 and T-4307
Delivery Schedule “C” – 48 weeks

	Steel Traffic Signal Standard Type SC (includes anchorage)
	2007 Standard Electrical Details T-1107 and T-4307
Delivery Schedule “C” – 48 weeks

	Traffic Signal Steel Arm 20 Foot
	2007 Standard Electrical Details T-1307
Delivery Schedule “C” – 48 weeks

	Traffic Signal Steel Arm 25 Foot
	2007 Standard Electrical Details T-1307
Delivery Schedule “C” – 48 weeks

	Traffic Signal Steel Arm 30 Foot
	2007 Standard Electrical Details T-1307
Delivery Schedule “C” – 48 weeks

	Traffic Signal Steel Arm 35 Foot
	2007 Standard Electrical Details T-1307
Delivery Schedule “C” – 48 weeks

	Traffic Signal Steel Arm 40 Foot
	2007 Standard Electrical Details T-1307
Delivery Schedule “C” – 48 weeks

	Traffic Signal Steel Arm 45 Foot
	2007 Standard Electrical Details T-1307
Delivery Schedule “C” – 48 weeks

	Traffic Signal Steel Arm 50 Foot
	2007 Standard Electrical Details T-1307
Delivery Schedule “C” – 48 weeks

	Steel Traffic Signal Standard Type SC Lighting Arm 15 Foot
	2007 Standard Electrical Details T-1307
Delivery Schedule “C” – 48 weeks

	Steel Traffic Signal Standard Type SC Lighting Arm 20 Foot
	2007 Standard Electrical Details T-1307
Delivery Schedule “C” – 48 weeks

	Steel Traffic Signal Anchorage
	2007 Standard Electrical Details T-4307
Delivery Schedule “C” – 48 weeks



[bookmark: _Toc161140872]4.7    SECTION F - CABINETS AND CABINET HARDWARE

	Descriptions

	Paint Adder Cabinet
	Cabinets and Cabinet Hardware
Delivery Schedule “C” – 48 weeks

	Meter Cabinet Type T
	DOT Spec Drawing P-0489
2007 Standard Electrical Details T-1907
Delivery Schedule “B” – 24 weeks

	Meter Cabinet Type T (Sheet Metal)
	2007 Standard Electrical Details T-3507
Delivery Schedule “B” – 24 weeks

	Meter Cabinet Fabricated Type (53 inch)
	DOT Sketch # 11
Delivery Schedule “B” – 24 weeks

	Meter Cabinet Type M (Sheet Metal)
	2007 Standard Electrical Details L-1407
Delivery Schedule “B” – 24 weeks

	Cabinet Type P
	DOT Sketch # 6
Delivery Schedule “B” – 24 weeks

	Cabinet Type P Split Skirt
	DOT Sketch # 7
Delivery Schedule “B” – 24 weeks

	Cabinet Type P Skirt
	DOT Sketch # 7
Delivery Schedule “B” – 24 weeks

	Meter Cabinet Type M (Lock and Keys)
	2007 Standard Electrical Details L-1407
Delivery Schedule “B” – 24 weeks

	Controller Cabinet (Lock and Key S591)
	DOT Sketch # 8
Delivery Schedule “B” – 24 weeks



[bookmark: _Toc161140873]4.8    SECTION G - SIGNS AND SIGN BRACKETS

	Descriptions

	Sign RED SIGNAL AHEAD - LED
	2007 Standard Electrical Details T-1407
Delivery Schedule “B” – 24 weeks

	NO LEFT TURN
	2007 Standard Electrical Details T-1407
Delivery Schedule “B” – 24 weeks

	NO RIGHT TURN
	2007 Standard Electrical Details T-1407
Delivery Schedule “B” – 24 weeks

	Blank Out Sign LED NO TURN on RED
	2007 Standard Electrical Details T-1407
DOT Sketch # 10
BME-LED-NTBLO Dated 6/23/08
Delivery Schedule “B” – 24 weeks

	Blank Out Sign (Message to be Determined when Ordered)
	2007 Standard Electrical Details T-1407
DOT Sketch # 10
BME-LED-NTBLO Dated 8/31/18
Delivery Schedule “B” – 24 weeks



[bookmark: _Toc161140874]4.9    SECTION H - SIGNAL CONTROL DEVICES

	Descriptions

	Detector (Microwave)
	TC-26B
Delivery Schedule “A” – 16 weeks

	Detector (Microwave)
	TC-30
Delivery Schedule “B” – 24 weeks

	Loop Detector 4 Channel
	NJDOT SPEC EB-LD-3
Delivery Schedule “A” – 16 weeks

	Detector Card
	NJDOT SPEC EB-LD-CARD
Delivery Schedule “A” – 16 weeks

	Uninterruptable Power System 850 Watts
	NJDOT SPEC BME-UPS-1
Dated 9/22/2014
Delivery Schedule “A” – 16 weeks



[bookmark: _Toc161140875]4.10    SECTION I - MISCELLANEOUS SIGNAL PRODUCTS DEVICES

	Descriptions

	Wireless Transceiver System -2
	Delivery Schedule “B” – 24 weeks

	Wireless Transceiver System -3
	Delivery Schedule “B” – 24 weeks

	Backplate – 8” Signal Head
	2007 Standard Electrical Details T-1807
Delivery Schedule “A” – 16 weeks

	Backplate – 12” Signal Head
	2007 Standard Electrical Details T-1807
Delivery Schedule “A” – 16 weeks

	Plastic Door Transformer Base TB-20
	2007 Standard Electrical Details T-0207
Delivery Schedule “A” – 16 weeks

	Plastic Door Pedestrian Signal Standard
	2007 Standard Electrical Details T-0707
Delivery Schedule “A” – 16 weeks

	Plastic Door Transformer Base K
	2007 Standard Electrical Details T-1007
Delivery Schedule “A” – 16 weeks

	Plastic Door Transformer Base TB-30
	2007 Standard Electrical Details L-1507
Delivery Schedule “A” – 16 weeks

	Plastic Door Transformer Base TB-17
	2007 Standard Electrical Details L-2107
Delivery Schedule “A” – 16 weeks

	GPS Time Reference
	Delivery Schedule “B” – 24 weeks



[bookmark: _Toc161140876]4.11    SECTION J - TRAFFIC SIGNAL CABLE

	Descriptions

	Traffic Signal Cable 2/C #14
	NJDOT SPEC BME-TS-CABLE
Dated July 1, 2008
Delivery Schedule “A” – 16 weeks

	Traffic Signal Cable 5/C #14
	NJDOT SPEC BME-TS-CABLE
Dated July 1, 2008
Delivery Schedule “A” – 16 weeks

	Traffic Signal Cable 7/C #14
	NJDOT SPEC BME-TS-CABLE
Dated July 1, 2008
Delivery Schedule “A” – 16 weeks

	Traffic Signal Cable 10/C #14
	NJDOT SPEC BME-TS-CABLE
Dated July 1, 2008
Delivery Schedule “A” – 16 weeks

	Traffic Signal Cable 14/C #14
	NJDOT SPEC BME-TS-CABLE
Dated July 1, 2008
Delivery Schedule “A” – 16 weeks



[bookmark: _Toc529958831][bookmark: _Toc51168005][bookmark: _Toc161140877]4.12    GENERAL REQUIREMENTS
All price line items reference New Jersey, Department of Transportation (NJDOT) specification/drawing numbers. These specification/drawing numbers are issued by NJDOT’s, Bureau of Electrical Engineering dated July 1, 2001 or as noted otherwise on the price line items listed on the State-Supplied Price Sheet.  

Specifications and/or drawings listed in this Bid Solicitation are available from NJDOT by contacting Mr. Dan Black at e-mail address:  Dan.Black@dot.nj.gov.  

NJDOT’s physical address is:

New Jersey Department of Transportation, 1035 Parkway Avenue, Trenton, NJ, 08618

Appointments for this purpose must be made prior to arriving at the NJDOT location by contacting Mr. Dan Black for a suitable date and time for the collection of the specifications/drawings pertaining to this Bid Solicitation.  Please note that contact must be limited to the appointment for the pick up of specifications/drawings only.  Any procurement-related questions will not be answered.  Please refer to Bid Solicitation Section 2.1 (Electronic Question and Answer Period) for the procedure involving questions and answers regarding the Bid Solicitation

Bid Solicitation Attachment #5 provides sketches referenced on the State-Supplied Price Sheet accompanying this Bid Solicitation.

All materials must meet specification requirements and any other specifications, sketches, drawings and/or manufacturer part numbers referenced in this Bid Solicitation.  

[bookmark: _Toc529958832][bookmark: _Toc51168006][bookmark: _Toc161140878]4.13    TECHNICAL SPECIFICATIONS
In addition to meeting the drawings, sketches and specifications referenced in this Bid Solicitation, the following additional requirements for items as noted must be met.

[bookmark: _Toc529958833][bookmark: _Toc51168007][bookmark: _Toc161140879]4.14    SECTION A - TRAFFIC SIGNAL INDICATIONS/PARTS

[bookmark: _Toc529958834][bookmark: _Toc51168008][bookmark: _Toc161140880]4.14.1    SPECIFICATIONS FOR TRAFFIC SIGNAL VISORS  (PRICE LINES 1 AND 2)

NJ SPECIFICATION NO. BME-TS-VISOR – EFFECTIVE DATE:  April 28, 2010

The intent and purpose of the following New Jersey Department of Transportation Specifications  are to describe the minimum acceptable requirements for Traffic Signal Visors.

[bookmark: _Toc529958835][bookmark: _Toc51168009]GENERAL – I

1-1	Traffic Signal Visors shall conform to the following:

A. Manual on Uniform Traffic Control Devices (MUTCD).

B. One piece construction.

C. Twist on mounting tabs.


[bookmark: _Toc529958836][bookmark: _Toc51168010]CONSTRUCTION - II

2-1 The polycarbonate traffic signal visors shall have twist on mounting tabs and shall be eight inch (8”) long open-bottom tunnel type for eight inch (8”) heads and ten inch (10”) long, tunnel type for twelve inch (12”) heads. Visor shall be tilted downward seven (7) degrees from horizontal.

2-2 The color shall be highway yellow matching to Fed.-Std.-595B color #13538. The inside surface of the visor shall be a dull non-reflective black

[bookmark: _Toc529958837][bookmark: _Toc51168011]INSTRUCTIONS AND GUARANTEE – III

The traffic signal visors shall carry a one (1) year guarantee from the date of delivery against any imperfections in workmanship and material.

[bookmark: _Toc529958838][bookmark: _Toc51168012][bookmark: _Toc161140881]4.15    SPECIFICATIONS FOR SCOOP VISORS  (PRICE LINE 3)

NJ SPECIFICATION NO. BME-TS-SCOOP VISOR – EFFECTIVE DATE:   May 31, 2018

The intent and purpose of the following New Jersey Department of Transportation Specifications are to describe the minimum acceptable requirements for Scoop Visors.

New Jersey Department of Transportation Specifications for Scoop Visors:

[bookmark: _Toc529958839][bookmark: _Toc51168013]GENERAL – I

1-1 Traffic Signal Scoop Visors shall conform to the following:

A. Manual on Uniform Traffic Control Devices (MUTCD)

[bookmark: _Toc529958840][bookmark: _Toc51168014]CONSTRUCTION - II

2-1 The aluminum tunnel visors shall have twist on mounting tabs, a louvered top with an open bottom and shall be 10.5 inches long for the twelve inch (12”) heads.

2-2 The louvered top slot shall be eight inches (8”) wide by four inches (4”) deep by 1,5 inches high.

2-3	The color shall be highway yellow matching to Fed.-Std.-595B color #13538. The inside surface of the visor shall be a dull non-reflective black.

[bookmark: _Toc529958841][bookmark: _Toc51168015]CONSTRUCTION - III

3-1 No changes or substitutions in these requirements will be accepted unless authorized in writing by the Director.

3-2 The signal face shall carry a one (1) year guarantee from the date of delivery against any imperfections in workmanship and material.

[bookmark: _Toc529958842][bookmark: _Toc51168016]Geometrically Programmed Louver (PRICE LINE 4)

Plastic twelve inches (12”) Indication NJDOT Sketch #1, The geometrically programmed louver shall be supplied with a slotted full circle visor.  The louver and visor shall be polycarbonate plastic. The louver shall be easily adjustable for either horizontal or vertical lane control with view angles adjustable from seven (7) degrees to forty - two (42) degrees. The assembly shall easily retrofit onto an existing signal indication.

[bookmark: _Toc529958843][bookmark: _Toc51168017][bookmark: _Toc161140882]4.16    SPECIFICATIONS FOR ADJUSTABLE FACE VEHICLE TRAFFIC CONTROL POLYCARBONATE SIGNAL HEAD (HOUSING ONLY) - (PRICE LINES 5 AND 6)

NJ SPECIFICATION NO. BME-TS-HEAD – EFFECTIVE DATE:  April 26, 2007

The intent and purpose of the following New Jersey Department of Transportation Specifications are to describe the minimum acceptable requirements for Adjustable Face Vehicle Traffic Control Polycarbonate Signal Head (Housing Only).

New Jersey Department of Transportation Specifications for Adjustable Face Vehicle Traffic Control Polycarbonate Signal Head (Housing Only).

[bookmark: _Toc529958844][bookmark: _Toc51168018]GENERAL – I

1-1 Vehicle traffic control heads shall conform to the following:

A. Manual on Uniform Traffic Control Devices (MUTCD)

B. Adjustable Face Vehicle Traffic Control Head Standard Institute of Transportation Engineers (ITE)

C. Standard Publication No. TS 1
National Electrical Manufacturer’s Association (NEMA)

CONSTRUCTION - II

2-1 Traffic signal heads shall allow the installation of LED modules without any modification to the signal head.

2-2 Traffic signal heads shall be a combination of signal faces of 8 inch or 12 inch signal sections as specified on the contract documents (or bid documents).

2-3 The housing of each section shall be a one-piece molded, ultraviolet and heat stabilized, flame retardant, permanently colored polycarbonate unit. The thickness  of  the housing shall be a minimum of .090 inches thick. All sections shall be identical and interchangeable with each other and shall be so designed that they interlock with each other forming a weatherproof assembly. Hinges or lugs shall be located inside each section for attaching the reflector assembly.

2-4 The housing door of each section shall be a one-piece, molded, ultraviolet and heat stabilized, flame retardant, permanently colored polycarbonate unit with an opening of sufficient diameter to accommodate the lens. On one side of the door, at top and bottom, there shall be a hinge so as to insure perfect alignment of the door. On the opposite side of the door, there shall be a wing nut assembly locking device to insure even gasket pressure. Twelve (12) inch signal sections shall be secured with two wing nut assemblies. Hinge pins and locking device shall be stainless steel.

2-5 The polycarbonate visors shall be twist or screw-on type and shall be eight inches (8”) long open-bottom tunnel type for eight inches (8”) heads and ten inch (10”) long, tunnel type for twelve inch (12”) heads. Visor shall be tilted downward seven (7) degrees from horizontal.

2-6 The color shall be highway yellow matching to Fed.-Std.-595B color #12538. The inside surface of the visor shall be a dull non-reflective black.

2-7 The top and bottom of the section shall be provided with positive, interlocking and indexing ring integral with the section. The integral locking ring shall consist of a single solid or double ring with seventy-two (72) teeth and a minimum width of one quarter inch (1/4”). Openings in top and bottom of the section(s) shall accommodate 1-1/2 standard pipe nipples.

2-8 All screws, washers, nuts and bolts shall be stainless steel. All components shall be readily accessible when the door is opened. Maintenance and/or replacement of components shall be completed using standard tools.

[bookmark: _Toc529958845][bookmark: _Toc51168019]ELECTRICAL - III

3-1	Each signal head shall be equipped with a barrier-type terminal block providing separate Screws for each signal section and neutral wires. For all multi-section signal heads, the terminal block shall be installed in the section with the yellow module. Each signal section shall be wired complete to the terminal block using color coded spade lugs.

[bookmark: _Toc529958846][bookmark: _Toc51168020]INSTRUCTIONS AND GUARANTEE – IV

4-1 Upon request, one wiring diagram and installation manual shall be provided with each signal face.

4-2 No changes or substitutions in these requirements shall be accepted unless authorized in writing by the Director.

4-3 The signal face shall carry a one (1) year guarantee from the date of delivery against any imperfections in workmanship and material.

[bookmark: _Toc161140883]4.17    SPECIFICATION FOR A LED (LIGHT EMITTING DIODE) HAND/MAN PEDESTRIAN SIGNAL MODULE (PRICE LINE 7)

N.J. SPECIFICATION NO. BME-TS-HAND/MAN  	EFFECTIVE DATE: MAY 25, 2010
The New Jersey Department of Transportation, Bureau of Maintenance Support and Operations Specification for a LED (Light Emitting Diode) hand/man pedestrian signal housing.
The purpose of this specification is to describe minimum performance/acceptable requirements for a LED (Light Emitting Diode) “walking person” and “hand” pedestrian signal housing.

[bookmark: _Toc529958847][bookmark: _Toc51168021]GENERAL – I

1-1 Hand/Man traffic control heads shall conform to the following:

A. Manual on Uniform Traffic Control Devices (MUTCD)

B. Adjustable Face Vehicle Traffic Control Head Standard Institute of Transportation Engineers (ITE)

C. Standard Publication No. TS 1
National Electrical Manufacturer’s Association (NEMA)

D. The housing size shall be 16 x 18 inches.

CONSTRUCTION – II

2-1 Hand/Man traffic signal heads - (PRICE LINE 7) shall allow the installation of LED modules without any modification to the signal head.

2-2 The housing section shall be a one-piece molded, ultraviolet and heat stabilized, flame retardant, permanently colored, polycarbonate unit. The thickness of the housing shall be a minimum of .090 inches.

2-3 The housing door shall be a one-piece, molded, ultraviolet and heat stabilized, flame retardant, permanently colored, polycarbonate unit with an opening of sufficient diameter to accommodate the lens. On one side of the door, at top and bottom, there shall be a hinge so as to insure perfect alignment of the door. On the opposite side of the door, there shall be a wing nut assembly locking device to insure even gasket pressure. Hinge pins and locking device shall be stainless steel.

2-4 The color shall be highway yellow matching to Fed.-Std.-595B color #12538. The inside surface of the visor shall be a dull non-reflective black.

2-5 The top and bottom of the housing section shall be provided with positive interlocking and indexing ring integral with the section. The integral locking ring shall  consist of a  single solid or double ring with seventy-two (72) teeth and a minimum width of ¼ inch. Openings in top and bottom of the section(s) shall accommodate 1-1/2 inch standard pipe nipples.

2-6 The door shall incorporate a visor screen to provide maximum sun and vandal protection. The screen (egg crate) shall be a molded, one piece network of equally spaced horizontal and diagonal louvers, approximately one (1) inch deep with a .030 inch nominal thickness. The screen may be molded into the door assembly or shall be attached internally using stainless steel screws.

2-7 All screws, washers, nuts and bolts shall be stainless steel. All components shall be readily accessible when the door is opened. Maintenance and/or replacement of components shall be done using standard tools.

ELECTRICAL – III

3-1	Each signal head shall be equipped with a barrier-type terminal block providing separate screws for the Hand/Man and neutral wires and shall be wired complete to the terminal block using color coded spade lugs.

INSTRUCTIONS AND GUARANTEE – IV

4-1 Upon request, one wiring diagram and an installation manual shall be provided with each signal face.

4-2 No changes or substitutions in these requirements shall be accepted unless authorized in writing by the Director.

The signal face shall carry a one (1) year guarantee from the date of delivery against any imperfections in workmanship and material.

[bookmark: _Toc529958848][bookmark: _Toc51168022][bookmark: _Toc161140884]4.18    SPECIFICATIONS FOR VISOR SCREEN (EGG CRATE) - (PRICE LINE 8)

N.J. SPECIFICATION NO. BME-TS-VSEC – EFFECTIVE DATE:  May 31, 2018

New Jersey Department of Transportation Specifications for a Visor Screen (egg crate).

The purpose of these specifications is to describe minimum acceptable requirements for Adjustable Face Hand/Man traffic control Polycarbonate Signal Head (Housing Only).

GENERAL - I

1-1	The visor screen (egg crate) shall conform to the following:

The visor screen (egg crate) shall be a molded, one piece network of equally spaced horizontal and diagonal louvers approximately one inch deep with a .030 inch nominal thickness. The visor screen shall be attached internally using stainless steel screws.

CONSTRUCTION – II

2-1	The visor screen (egg crate) shall be installed without any modification to the signal head.

2-3 The visor screen shall fit into a 16” x 18” housing.

INSTRUCTIONS AND GUARANTEE – III

3-1	No changes or substitutions in these requirements will be accepted unless authorized in writing by the Director.

3-2	The signal face shall carry a one year guarantee from the date of delivery against any imperfections in workmanship and material.

3M R.A.G. (PRICE LINE 9) (3 Section – 12”) – Specifications are described in the NJDOT spec drawing EB-TS-2, which can be located on the NJDOT website at http://www.state.nj.us/transportation/eng/elec/TSS/english/ 

3M ARROW (PRICE LINE 10) (1 Section) – Specifications are described in the NJDOT spec drawing EB-TS-2; Section G, which can be located on the NJDOT website at http://www.state.nj.us/transportation/eng/elec/TSS/english/ 

[bookmark: _Toc161140885]4.19    SECTION B - TRAFFIC SIGNAL HANGERS/BRACKETS
Sign Bracket 2007 Standard Electrical Details T-4507 (PRICE LINES 11 AND 12).  The State reserves the right to order different support pipe lengths as long as the average length of the support pipe for a particular order is forty-two (42) inches or shorter.  For example, the State can order five (5) offset sign brackets for 36” signs at the Unit Price awarded to the Contractor for this item.

Adapter – Pedestal (Slip fitter) with Brass Chase Nipple (PRICE LINE 13) – 2007 Standard Electrical Details T-0607 and T-0707.

Adapter – Pedestal (Offset Slip fitter) with Brass Chase Nipple (PRICE LINE 14) – NJDOT Sketch # 2

Band Bracket Assembly (PRICE LINE 17) – Midarm 8” – 12” Indication – 2007 Standard Electrical Details T-2107.

Cable Bracket Assembly – Midarm 8” or 12” Indication (PRICE LINE 18) – 2007 Standard Electrical Details T-2107.

Clevis – H Mast Arms (PRICE LINE 19) - 2007 Standard Electrical Details T-0407 (Universal Joint) Mast Arm Slip fitter (PRICE LINE 20) - 2007 Standard Electrical Details T-0407 (Mast Arm Slip fitter)

Universal Joint and Wire Outlet with S/S Hardware (PRICE LINE 21) -2007 Standard Electrical Details T-0407 (Universal Joint and Wire Outlet) One (1) serrated positioning ring shall be provided with each universal joint and wire outlet in addition to all other material and requirements as detailed on Drawing T-0407.

Pedestrian Clamp Type Assembly for Approx. 7-1/2” Dia. Pole – 12” STD Nipple (PRICE LINE 22) – 2007 Standard Electrical Details T-0607

Pedestrian Clamp Type Assembly for Approx. 9-1/2” Dia. Pole (PRICE LINE 23)  – 12” STD Nipple – 2007 Standard Electrical Details T-0607

Two-way bracket Assembly with T-Bar (PRICE LINE 26) – 2007 Standard Electrical Details T-0507 (Hollow Spider for 2-way Assembly and T-Bar)

Three-way bracket Assembly (PRICE LINE 27) – 2007 Standard Electrical Details T-0507 (Hollow Spider for 3-way Assembly)

Four-way bracket Assembly (PRICE LINE 28) – 2007 Standard Electrical Details T-0507 (Hollow Spider for 4-way Assembly)

Pole Clamp Assembly, Hinge Strap Type (PRICE LINE 29) – 12” Standard Nipple – 2007 Standard Electrical Details T- 0607 (Pole Clamp Assembly Hinge Strap Type). For the item pole clamp assembly- hinge strap type, the pole clamp assembly must be supplied completely assembled ready for mounting on a standard Type "K" traffic signal pole. The assembly shall consist of all items noted in the hinge strap list of materials for mounting a single (one-way) traffic signal indication.

Traffic Signal Safety Chain (PRICE LINE 30) – 2007 Standard Electrical Details T-0307 and T-0907. The safety chain must be supplied and shipped as a complete unit with the bolt, washers and nuts secured through the safety chain.

[bookmark: _Toc161140886]4.20    SECTION C - TRAFFIC SIGNAL POLES, ARMS BASES
Paint Adder for Poles, Arms, Bases (PRICE LINES 31, 32 AND 33) - The Poles, Arms and Bases shall be prepared for powder coating first by chemical etching, using a caustic solution followed by neutralizing then water rinse. Powder coating material shall be a thermosetting polyester powder coating.  A minimum coating thickness of 1½ mils shall be maintained. Application of powder shall be electrostatically applied by a closed loop powder coating system featuring automatic spray guns with computerized controls to assure mil thickness conformance. Standard colors should be used and will be specified at time of order.

TB-20 Base (PRICE LINE 34) – 2007 Standard Electrical Details T-0207. A plastic transformer base door must be supplied.

HHB Base (PRICE LINE 35) – 2007 Standard Electrical Details L-1507. A plastic transformer base door must be supplied.

K Base (PRICE LINE 36) – 2007 Standard Electrical Details T-1007. A plastic transformer base door must be supplied.

Traffic Signal Pole Type T (PRICE LINE 37) – 2007 Standard Electrical Details T-0107

Traffic Signal Pole Type C (PRICE LINE 38) – 2007 Standard Electrical Details T-0807

Traffic Signal Pole Type K (PRICE LINE 39) – 2007 Standard Electrical Details T-1007

Pedestal Pole 8 Foot (PRICE LINE 40) – 2007 Standard Electrical Details T-0707 Pedestal

Pole 12 Foot (PRICE LINE 41) – 2007 Standard Electrical Details T-0707

Traffic Signal Standard Type KE (PRICE LINE 42) – 2007 Standard Electrical Detail T-1007

Traffic Signal Standard Type KE Mounting Adapter for Mongoose Luminaire (PRICE LINE 43) – DOT SKETCH #3 

Traffic Signal Standard Type K Mounting Adapter for Mongoose Luminaire (PRICE LINE 44) – NJDOT SKETCH #4 

Traffic Signal Mast Arm 15 Foot Trombone (PRICE LINE 45) – 2007 Standard Electrical Details T-1207

Traffic Signal Mast Arm 20 Foot Trombone (PRICE LINE 46) – 2007 Standard Electrical Details T-1207

Traffic Signal Mast Arm 15 Foot (PRICE LINE 47) – 2007 Standard Electrical Details T-0307

Traffic Signal Mast Arm 20 Foot (PRICE LINE 48) – 2007 Standard Electrical Details T-0307

Traffic Signal Mast Arm 25 Foot (PRICE LINE 49) – 2007 Standard Electrical Details T-0307

Traffic Signal Mast Arm 15 Foot Type K (PRICE LINE 50) – 2007 Standard Electrical Details T-0907

Traffic Signal Mast Arm 20 Foot Type K (PRICE LINE 51) – 2007 Standard Electrical Details T-0907

Traffic Signal Mast Arm 25 Foot Type K (PRICE LINE 52) – 2007 Standard Electrical Details T-0907

Traffic Signal Standard Type T Pole Cap (PRICE LINE 53) – 2007 Standard Electrical Details T-0107 Detail “B”

Traffic Signal Standard Type K Pole Cap (PRICE LINE 54) – 2007 Standard Electrical Details T-1007 Detail “C”

[bookmark: _Toc161140887]4.20.1    POLE IDENTIFICATION
a.	For traffic signal pole (Type T, Type C and Type K) and for traffic signal standard, Type KE, the following tag identification shall be utilized:

1) An identification tag shall be welded on the inside of the pole three to five inches (3-5”) from the base. The tag shall be welded upside down so that the lettering “NJDOT” is not visible but instead facing into the pole.

b.	For pedestal pole (8 foot and 12 foot) the following tag identification must be provided:

1) An identification tag shall be welded on to the member of the arm, three to five inches (3-5”) away from the weld of the clamp assembly. The tag shall be welded upside down so that the lettering “NJDOT” is not visible but instead facing into the pole.

c.	For traffic signal mast arm (Trombone 15 foot, Trombone 20 foot, 15 foot, 20 foot, 25 foot, 15 foot type K, 20 foot Type K and 25 foot Type K) (PRICE LINES 42 THROUGH 52) the following tag identification must be provided:

1) An identification tag shall be welded on to the member of the arm, three to five inches (3-5”) away from the weld of the clamp assembly. The tag shall be welded upside down so that the lettering “NJDOT” is not visible but instead facing into the pole.

[bookmark: _Toc161140888]4.20.2    TAG IDENTIFICATION
a.	Tag Construction

1) The tag shall be manufactured from an aluminum allow #6063-T6.  The dimensions shall be 2 to 2-1/2 inches in length, ¾ inches in width and 1/8 inches thick. The lettering shall be 3 inches with “NJDOT” indented in the center of the tag.

b.	Verification by the Using Agency

1) If improper identification is discovered after the poles are delivered to the Using Agency, the Contractor must follow the instructions in Bid Solicitation Section 4.50.  Payment will not be processed until the Contractor, through the manufacturer, properly tags and identifies the material per these specifications.  The Using Agency will hold the supplier responsible for the entire shipment even if only one tag is not lettered properly.

c.	Code Identification

1) All items in this Bid Solicitation, except the following items, shall have the Bid Solicitation number marked on it in black indelible ink. The lettering shall be at least ¼ inch. The location is at the discretion of the Contractor “Traffic Signal Pedestal – 8’ and “Traffic Signal Pedestal – 12’ shall have the Bid Solicitation number cast into the item with the lettering at least ¼ inch. The location is at the discretion of the Contractor.

[bookmark: _Toc161140889]4.21    SECTION D - LIGHTING POLES, ARMS, BASES
Paint Adder for Poles and Arms Bases (PRICE LINE 55) – The poles, arms and bases shall be prepared for powder coating first by chemical etching, using a caudtic solution followed by neutralizing then water rinse. Powder coating material shall be a thermosetting polyester powder coating.  A minimum coating thickness of 1½ mils shall be maintained.  Application of powder shall be electrostatically applied by a closed loop powder coating system featuring automatic spray guns with computerized controls to assure mil thickness conformance.  Standard Colors should be used and will be specified at time of order.

Lighting Pole Type L (PRICE LINE 56) – NJDOT Spec. Drawing P-0189

Lighting Pole Type L-40 (PRICE LINE 57) – NJDOT Spec. Drawing P-0289

Lighting Arm 8 Foot (PRICE LINE 58) – NJDOT Spec. Drawing P-0389 Lighting

Arm 15 Foot (PRICE LINE 59) – NJDOT Spec. Drawing P-0389

Transformer Base – Lighting (PRICE LINE 60)  – 2007 Standard Electrical Details L-2107. A plastic transformer base door must be supplied.

Lighting Arm Assembly (PRICE LINE 63) – NJDOT SKETCH #5

Mounting Adapter for Offset Luminaire (PRICE LINE 64) – 2007 Standard Electrical Details L-1807

[bookmark: _Toc161140890]4.21.1    POLE IDENTIFICATION
a.	For items lighting pole (Type L, Type L-40) the following tag identification must be provided:

1) An identification tag shall be welded on the inside of the pole 3-5 inches from the base. The tag shall be welded upside down so that the lettering “NJDOT” is not visible but instead facing into the pole.

b.	For items lighting arm (8 foot and 15 foot) the following tag identification must be provided:

1) An identification tag shall be welded onto the member of the arm, 3-5 inches away from the weld of the clamp assembly. The tag shall be welded upside down so that the lettering “NJDOT” is not visible but instead facing into the pole.

[bookmark: _Toc161140891]4.21.2    TAG IDENTIFICATION
a.	Tag Construction

1) If improper identification is discovered after the poles are delivered to the Using Agency, the Contractor will be must follow the instructions in Bid Solicitation Section 4.50.  Payment will not be processed until the Contractor, through the manufacturer, properly tags and identifies the material per these specifications.  The Using Agency will hold the supplier responsible for the entire shipment even if only one tag is not lettered properly.

b.	Verification by the Using Agency

1) If improper identification is discovered after the poles are delivered to the Using Agency, the Contractor will be held responsible. Payment will not be processed until the Contractor, through the manufacturer, properly tags and identifies the material per these specifications. The Using Agency will hold the Contractor responsible for the entire shipment even if only one tag is not lettered properly.

c.	Code Identification

1) All items in this bid shall have the bid number marked on it in black indelible ink. The lettering shall be at least 1/4 inch. The location is at the discretion of the Contractor.

The vibration damper shall include all necessary mounting hardware.  Mounting hardware shall be stainless steel.

[bookmark: _Toc161140892]4.22    SECTION E - STEEL TRAFFIC SIGNAL POLES AND ARMS
Steel Traffic Signal Standard (includes anchorage) (PRICE LINE 65) – 2007 Standard Electrical Details T-1107 and T-4307. Steel Poles shall be supplied with anchorage (anchor bolts, hex nuts, lock washers and flat washers) as detailed and required.

The Alternate pole top to be supplied shall be supplied with the Traffic Signal Standard, Type S poles for the Mongoose lighting fixture and shall include a two (2) inch Schedule  80  Tenon  at least 6 inches above the top plate.  NJDOT Sketches #3 and #4 are to be utilized as references for the adapters.

Steel Traffic Signal Standard Type SC (includes anchorage) (PRICE LINE 66) – 2007 Standard Electrical Details T- 1107 and T-4307. Steel Poles shall be supplied with anchorage (anchor bolts, hex nuts, lock washers and flat washers) as detailed and required. The Alternate pole top to be supplied shall be supplied with the Traffic Signal Standard, Type SC poles for the Mongoose lighting fixture and shall include a two (2) inch Schedule 80 Tenon at least 6 inches above the top plate.  NJDOT Sketches #3 and #4 are to be utilized as references for the adapters.

Traffic Signal Steel Arm 20 Foot (PRICE LINE 67) – 2007 Standard Electrical Details T-1307. Steel mast arms shall be supplied with all clamps attached to arm with all connecting hardware (hex head bolts, nuts and washers) as required by the manufacturer to install the pole and mast arm as a unit.

Traffic Signal Steel Arm 25 Foot (PRICE LINE 68) – 2007 Standard Electrical Details T-1307. Steel mast arms shall be supplied with all clamps attached to arm with all connecting hardware (hex head bolts, nuts and washers) as required by the manufacturer to install the pole and mast arm as a unit.

Traffic Signal Steel Arm 30 Foot (PRICE LINE 69) – 2007 Standard Electrical Details T-1307. Steel mast arms shall be supplied with all clamps attached to arm with all connecting hardware (hex head bolts, nuts and washers) as required by the manufacturer to install the pole and mast arm as a unit.

Traffic Signal Steel Arm 35 Foot (PRICE LINE 70) – 2007 Standard Electrical Details T-1307. Steel mast arms shall be supplied with all clamps attached to arm with all connecting hardware (hex head bolts, nuts and washers) as required by the manufacturer to install the pole and mast arm as a unit.

Traffic Signal Steel Arm 40 Foot (PRICE LINE 71) – 2007 Standard Electrical Details T-1307. Steel mast arms shall be supplied with all clamps attached to arm with all connecting hardware (hex head bolts, nuts and washers) as required by the manufacturer to install the pole and mast arm as a unit.

Traffic Signal Steel Arm 45 Foot (PRICE LINE 72) – 2007 Standard Electrical Details T-1307. Steel mast arms shall be supplied with all clamps attached to arm with all connecting hardware (hex head bolts, nuts and washers) as required by the manufacturer to install the pole and mast arm as a unit.

Traffic Signal Steel Arm 50 Foot (PRICE LINE 73) – 2007 Standard Electrical Details T-1307. Steel mast arms shall be supplied with all clamps attached to arm with all connecting hardware (hex head bolts, nuts and washers) as required by the manufacturer to install the pole and mast arm as a unit.

Steel Traffic Signal Standard Type SC Lighting Arm 15 Foot (PRICE LINE 74) – 2007 Standard Electrical Details T- 1307. Steel mast arms shall be supplied with all clamps attached to arm with all connecting hardware (hex head bolts, nuts and washers) as required by the manufacturer to install the pole and mast arm as a unit.

Steel Traffic Signal Standard Type SC Lighting Arm 20 Foot (PRICE LINE 75) – 2007 Standard Electrical Details T- 1307. Steel mast arms shall be supplied with all clamps attached to arm with all connecting hardware (hex head bolts, nuts and washers) as required by the manufacturer to install the pole and mast arm as a unit.

Steel Traffic Signal Anchorage (PRICE LINE 76) – 2007 Standard Electrical Details T-4307

[bookmark: _Toc161140893]4.23    SECTION F - CABINETS AND CABINET HARDWARE
Paint Adder for Cabinets and Cabinet Hardware (PRICE LINES 79 AND 80) - The Cabinets and Cabinet Hardware shall be prepared for powder coating first by chemical etching, using a caustic solution followed  by neutralizing then water rinse.

Powder coating material shall be a thermosetting Polyester Powder Coating. A minimum coating thickness of 1½ mils shall be maintained. Application of powder shall be electrostatically applied by a closed loop powder coating system featuring automatic spray guns with computerized controls to assure mil thickness conformance. Standard Colors will be used and will be specified at time of order.

Meter Cabinet Type T (PRICE LINE 81)  – DOT Spec Drawing P-0489 and 2007 Standard Electrical Details T- 1907. A "cast" aluminum cabinet must be supplied.

Meter Cabinet Type T (Sheet Metal) (PRICE LINE 82) – 2007 Standard Electrical Details T-3507. A sheet aluminum cabinet must be supplied.

Meter Cabinet Fabricated Type (53 inch) (PRICE LINE 83) – NJDOT Sketch # 11.

Meter Cabinet Type M (Sheet Metal) (PRICE LINE 84) – 2007 Standard Electrical Details L-1407

Cabinet Type P (PRICE LINE 85) – NJDOT SKETCH #6

Cabinet Type P Slit Skirt (PRICE LINE 86) – The split skirt shall include a two-piece skirt of sheet aluminum with shelves. The skirt shall be an extension of the Traffic Signal P cabinet to contain batteries for the Uninterruptible Power System. The skirt manufacturer shall have a Traffic Signal, Type P Cabinet with an approved NJDOT EE Number. The height of the skirt shall be a minimum of 18 inches and the width shall be 26 inches and the length shall be 44 inches. The shelves shall be adjustable with the capacity to hold six UPS batteries. DOT SKETCH # 7.

Cabinet Type P Skirt (PRICE LINE 87) – The skirt shall include a skirt of sheet aluminum with shelves.  The skirt shall be an extension of the Traffic Signal P cabinet to contain batteries for the Uninterruptible Power System. The skirt manufacturer shall have a Traffic Signal, Type P Cabinet with an approved NJDOT EE Number.

The height of the skirt shall be a minimum of 18 inches and the width shall be 26 inches and the length shall be 44 inches. The shelves shall be adjustable with the capacity to hold six UPS batteries. NJDOT SKETCH # 7.

Meter Cabinet Type M Lock and Keys (PRICE LINE 88) – 2007 Standard Electrical Details L-1407

Controller Cabinet Lock and Keys S591 (PRICE LINE 90) – NJDOT SKETCH #8

[bookmark: _Toc161140894]4.24    SECTION G - SIGNS AND SIGN BRACKETS 
Sign RED Signal Ahead (PRICE LINE 91) – 2007 Standard Electrical Details T-1407. Changes to the 2007 detail are as follows: The “Signal Ahead” legend shall be Lunar White. The note for number of supports has been changed from “two” to as recommended by the sign manufacturer. The transformer and/or circuit board shall be enclosed in weather resistant material painted with high quality flat black paint.

[bookmark: _Toc161140895]4.24.1    SPECIFICATION FOR LED BLANK OUT SIGNS  (PRICE LINES 94 AND 95)

N.J. SPECIFICATION NO. BME-LED-NTBLO – EFFECTIVE DATE:  May 31, 2018

New Jersey Department of Transportation, Bureau of Maintenance Engineering Specification for a LED (light emitting diode) "NO TURN ON RED" and BLANK (Message to be determined when ordered) blank out sign.

It is the purpose of this specification to describe the minimum acceptable requirements for a LED (light emitting diode) "NO TURN ON RED" and BLANK (Message to be determined when ordered) blank out sign.

General – 1
1-1	The LED blank out sign that displays the “NO TURN ON RED” and BLANK (Message to be determined when ordered) shall have the display dimensions of 30 inches wide by 30 inches tall.

1-2	The LED blank out sign shall consist of the following:
A. Weather proof housing with door;
B. Faceplate with polycarbonate lens;
C. Visor (minimum depth of 6 inches);
D. Back plate;
E. Enclosed transformers and/or circuit board with weather resistant material painted with high quality flat black paint; and 
F. High output white LEDs.

1-3	The legend color shall be lunar white.

1-4	The formed letters shall conform to The United States Department of Transportation’s standard alphabet.

Construction – 2

2-1	The entire front face of the signal shall be protected by a sheet of polycarbonate mounted in the extruded aluminum doorframe. The lens material shall be 1/8 inch thick, clear polycarbonate with vandal resistant properties.

2-2	The sign shall include a 0.125 inch thick aluminum weatherproof housing and door. Closed cell neoprene gasketing shall be attached to the face of the enclosure to provide a weather- tight seal against the door.

2-3	The interior of the housing, visor and faceplate shall be acid etched and painted with two coats of zinc chromate primer and finished with two coats of high quality flat black enable to eliminate internal reflection. Two coats of yellow standard color No. 12538 baking enamel shall be used for exterior surfaces.

2-4	The housing shall be supplied with standard 1-1/2 inch N.P.T. (American National Pipe Tapered Thread) hubs, top and bottom.

2-5	The message shall be formed by single rows of high output LED’s spaced at ½” O.C. (On Center), nominal.

2-6	The signal shall completely blank out when not energized.

2-7	The sign shall be equipped with four 3/16 inch diameter weep holes located at the lower corners of the housing.

2-8	All mounting hardware (hinge pins, nuts, bolts, lock washers, etc.) shall be stainless steel. 

2-9	Access to the internal components shall be through a hinged doorframe.

Electrical – 3

3-1	The LED module shall be so designed that when operated over the specified ambient temperature and voltage range, the signal shall be readable, during daylight and nighttime conditions, between 10 feet and 150 feet.

3-2	AllnGap (aluminum indium gallium phosphorus) LEDs rated at 100,000 hours at 75° F and 20ma shall be utilized.

3-3	LED’s shall not exhibit degradation of more than 30% of their initial light intensity following accelerated life testing, 185° F at 85% relative humidity, operating for 1,000 hours, with a forward current of 10 milliamps.

3-4	The sign assembly shall connect directly to 120 volt AC nominal line voltage and shall be able to operate over a voltage range of 80 to 135 VAC. The variation in line voltage shall not cause the light intensity to vary by more than 10% over the entire voltage range.

3-5	The sign assembly shall operate over a temperature range of -35° F through +165° F.

3-6	The electrical connection shall be provided by a barrier type, closed back terminal strip.  Cable entrance shall be through a weather-resistant strain relief connector.

Instructions and Guarantee – 4

4-1	No changes or substitutions n these requirements will be accepted unless authorized in writing by the Director.

4-2	Each blank out sign shall carry a one-year guarantee from the date of delivery to cover any imperfections in material and workmanship.

4-3	The Contractor agrees to deliver a sample of the LED sign assembly to be supplied in compliance with these specifications for test before acceptance, if requested by NJDOT.  After evaluation, the sample will be returned.

Blank Out Sign LED NO RIGHT/LEFT TURN ON RED (PRICE LINES 92 AND 93) – 2007 Standard Electrical Details T-1407 and BME-LED-NTBLO Dated 5/31/18.  The International Symbol for No Right/Left Turn on Red is an acceptable alternative.

Blank Out Sign (MESSAGE TO BE DETERMINED WHEN ORDERED) PRICE LINE 95 – 2007   Standard Electrical Details T-1407, DOT SKETCH #10 and BME-LED-NTBLO Dated 5/31/18.

[bookmark: _Toc161140896]4.25    RESERVED.

Detector Microwave TC-26B (PRICE LINE 96) - The microwave sensor must be supplied with all mounting hardware required to install on standard New Jersey Department of Transportation Type "T" traffic signal pole. All mounting hardware (bolts, nuts, washers, banding, etc.) must be stainless steel.

Detector Microwave TC-30 (PRICE LINE 97) - The microwave sensor must be supplied with all mounting hardware required to install on standard New Jersey Department of Transportation Type "T" traffic signal pole. All mounting hardware (bolts, nuts, washers, banding, etc.) must be stainless steel.

Loop Detector 4 Channel – NJDOT Spec EB-LD-3 (PRICE LINE 98)

Detector Card – NJDOT Spec EB-LD-CARD  (PRICE LINE 99)

[bookmark: _Toc161140897]4.25.1    SPECIFICATION FOR TRAFFIC SIGNAL UNINTERRUPTIBLE POWER SUPPLY  (PRICE LINE 100)

N.J. SPECIFICATION NO. BME-UPS-1 – EFFECTIVE DATE:  September 22, 2014

The New Jersey Department of Transportation, Bureau of Maintenance Engineering Specification for an Uninterruptible Power Supply System.

It is the purpose of this specification to describe minimum acceptable requirements for an Uninterruptible Power Supply (UPS) system.

GENERAL – 1

1-1	The UPS system shall be comprised of the UPS module, a power management module (PMM), and/or a power interface module (PIM), butteries, and connecting harnesses.

1-2	The primary purpose of this equipment is to provide battery back-up in the event of a utility power failure or partial interruption. The switch-over from utility power failure or partial interruption to UPS shall occur with no interruption to the traffic signal.

1-3	The manufacturer, upon request, shall provide documentation from an independent laboratory pertaining to 1-3 and environmental and vibration testing as per NEMA TS standards.

1-4	When utility power is outside the user set points, the UPS inverter provides seamless output power from the batteries and switches the power management module to the UPS output. The power management unit contacts shall be user programmable to delay start from 0-8 hours when the system operates on battery.

1-5	When utility power returns to the user set points, the UPS will synchronize the inverter to the incoming utility AC power and provide seamless transfer back to the utility AC power and begin to re-charge the batteries.

ELECTRICAL/MECHANICAL – 2

2-1	The UPS shall be able to function properly in the input voltage range of 100 volts AC to 130 volts AC without switching over to battery power.

2-2	The UPS shall provide regulated power to any power factor 0 to 1, leading, lagging, or non- linear and shall be capable of handling non-symmetrical loads.

2-3	The operating temperature range shall be certified to operate from -35°F to +F (-37°C to +74°C), 5 to 95% relative humidity, non-condensing.

2-4	The output voltage regulation shall be 120 volts AC +/-3%.

2-5	The output of the unit shall produce less than 4% total Harmonic Distortion (THD).

2-6	The physical size of the UPS module shall not exceed 19” wide X 14” deep X 6” high.

2-7	Quick disconnect/locking connectors shall be utilized to ensure connection integrity and to prevent operation of the UPS without connection to the PMM and/or PIM shall be provided.

2-8	The power output shall exceed 850 watts with the frequency at 50 Hz or 60 Hz.

2-9	Advanced heat sink design shall be utilized to minimize the use of the cooling fan and to extend fan life.

2-10	The system shall comply with the lighting and surge protection standard, ANSI/EEE C.62.41/C.62.45 Cat A&B. Upon request, the Contractor shall provide compliance.

2-11	The UPS shall be equipped with protection on the inputs and outputs for shorts circuits and overloads.

[bookmark: _Toc161140898]4.25.2    POWER MANAGEMENT MODULE/POWER INTERFACE MODULE - 3
3-1	The PMM and/or PIM shall provide easy customer interface and can operate without disturbing power to the protected load while the UPS module is being “hot swapped”.

3-2	The PMM and/or PIM shall have three sets of independent auxiliary contacts for Flash, Delayed Flash and Monitoring the UPS.

3-3	Terminal blocks shall be provided for connecting the utility power input and the PMM and/or PIM output to the load.

Batteries – 4

4-1	Batteries shall be absorbed glass mat, non-spillable, valve regulated, and lead acid type with tongue/groove epoxy seal.

4-2	Batteries shall be capable of at a minimum to providing a typical 3-year average operating life.

4-3	All connections at the battery should be provided with factor sealed wire leads that include quick disconnects. All hardware shall be stainless steel.

4-4	Batteries are to be connected in parallel so as to provide redundancy should battery fail and to insure that each battery jar is equally charged. If batteries are connected in series to achieve the required operating voltages of the UPS, a parallel string of batteries shall also be provided.

UPS MODULE – 5

5-1	The UPS module shall be a digitally controlled microprocessor system with Transient Voltage Surge Suppression.

5-2	The front panel of the UPS module shall be equipped with alarm, battery level, and run time indicators, with two RS232 type data and signal ports as well as an electrical outlet.

5-3	The UPS module shall be able to provide the number of power utility failures.

5-4	The UPS module shall be able to be monitored by a Web based network interface.

5-5	The UPS module shall contain a 3-stagecharger to re-charge and to ensure batteries are maintained at full charge.

5-6	The UPS module shall be able to be replaced without shutting down the traffic controller system.

5-7	The UPS module shall contain a charger to recharge and to ensure batteries are maintained at full charge. The charger shall be capable of fully recharging the batteries from a depleted state after nit shutdown in approximately eight hours.

5-8	The UPS module shall have protection from brownout conditions and voltage spikes from the input voltage.

Instructions and Guarantee – 6

6-1	One wiring diagram and installation sheet shall be provided with each UPS system.

6-2	No changes or substitutions in these requirements shall be accepted unless authorized in writing by the Director.

6-3	The UPS system shall carry a two-year guarantee from the date of delivery against any imperfections in workmanship and material.

[bookmark: _Toc161140899]4.25.3    SPECIFICATIONS FOR WIRELESS CONTACT CLOSURE SYSTEM  (PRICE LINES 101 AND 102)

N.J. SPECIFICATION NO. BME-WCCS – EFFECTIVE DATE:  May 24, 2010

New Jersey Department of Transportation, Bureau of Maintenance Engineering Specification for a Wireless Contact Closure System.

It is the purpose of this specification to describe minimum acceptable requirements for a Wireless Contact Closure System.

GENERAL – 1

Enclosure Ruggedized extruded aluminum,
· Size H: 1.81” x W: 6.18” x L: 4.37” Weight 21.3 lbs.
· Temperature Operating Range -40º C to +75º C External Antenna N Type Female Setup/Diagnostic RJ12, (TXD, RXD, CTS, RTS, GND), DCE

Power Locking Receptacle (MOLEX® Mini-Fit Jr.)
· Input Voltage 900 MHz: 6-30 VDC 2.4 GHz: 9.5-30 VDC
· Operating Mode 900 MHz at 24 VDC (mA) 2.4 GHz at 24 VDC (mA)
· System Configurations Point-to-Point (bi-directional), Point-to-Multipoint (bi-directional), Multipoint- to- Point (bi-directional)
· Unit Operational Modes Base, Repeater, Remote, Remote/Repeater Range, Line of Sight 20 Miles
· Inputs 8 digital, 3-40 VDC, ground activated
· Outputs 8 digital, 550 mA Max Load current per output (mosfet open drain), 2 Amps total I/O Connector Type Quick release terminal block
· Indicators Power, Input, Output, Link User-defined output control Time based
· I/O Timing Specifications (bi-directional) Low Latency Mode Normal Mode Long Distance Mode End-to-End Change Latency (typical) bi-directional < 12 ms bi-directional < 14 ms bi-directional < 15 ms

The wireless contact closure units shall provide software programmable I/O mapping, two way communication, plug and play, point-to-point and point-to-multipoint configurations. The wireless contact closure units shall perform the following:

Vehicle Preemption, Fire Hall and Railroad Preemption, Advanced Vehicle Detection, Radar Solutions, Video Solutions, Loop Solutions, Ramp Metering, Variable Message Signs (VMS), School Zone Flashers / Advanced Warning Beacons

The spread spectrum wireless equipment can provide communications with the detectors in a variety of formats: Serial (RS-232), Ethernet (TCP/IP), and Contact Closures (I/0). All types of detection systems: Loop detectors, Video Detection Systems, and Radar/Microwave detectors are supported.

The Antenna Drop Down cable shall be 40 foot with appropriate connectors.

The wireless contact closure system shall include all necessary material/equipment for installation of a fully functioning system including the 36” tubes.

Backplate – 8” Signal Head (PRICE LINE 103) – 2007 Standard Electrical Details T-1807 

Backplate – 12” Signal Head (PRICE LINE 104) – 2007 Standard Electrical Details T-1807 

Plastic Door Transformer Base TB-20 (PRICE LINE 105) – The ABS plastic door shall fit the dimensions as per the 2007 Standard Electrical Details T-0207 and shall be modified for UV resistance. The door shall be Steel Gray Color and shall be attached to base with an approved vandal resistant locking device using a ¼” or 3/8” Stainless Steel Grade 88 Socket HD Cap Screw.

Plastic Door Transformer Base K (PRICE LINE 106) – The ABS plastic door shall fit the dimensions as per the 2007 Standard Electrical Details T-1007 and shall be modified for UV resistance. The door shall be Steel Gray Color and shall be attached to base with an approved vandal resistant locking device using a ¼” or 3/8” Stainless Steel Grade 88 Socket HD Cap Screw.

Plastic Door Transformer Base TB-30 (PRICE LINE 107) – The ABS plastic door shall fit the dimensions as per the 2007 Standard Electrical Details L-1507 and shall be modified for UV resistance. The door shall be Steel Gray Color and shall be attached to base with an approved vandal resistant locking device using a ¼” or 3/8” Stainless Steel Grade 88 Socket HD Cap Screw.

Plastic Door Transformer Base TB-17 (PRICE LINE 108) – The ABS plastic door shall fit the dimensions as per the 2007 Standard Electrical Details L-2107 and shall be modified for UV resistance. The door shall be Steel Gray Color and shall be attached to base with an approved vandal resistant locking device using a ¼” or 3/8” Stainless Steel Grade 88 Socket HD Cap Screw.

GPS Time Reference (PRICE LINES 115 AND 116) – Automatically reset time-of-day in controllers using GPS Technology. Programming set in circuit board. NO laptop or external programmers shall be allowed.  The unit shall have an easy to read LCD Display that allows the viewer to see the status, time and date and program running. There shall be a selection to allow you to reset the controller time on the Hour or the Half-hour, to allow for daylight savings time and to select the time zone. The GPS Time Reference shall come complete with all necessary hardware/equipment to install a fully functioning and operational unit.

[bookmark: _Toc161140900]4.26    SECTION J - TRAFFIC SIGNAL CABLE

[bookmark: _Toc161140901]4.26.1    SPECIFICATIONS FOR TRAFFIC SIGNAL CABLE  (PRICE LINES 117 THROUGH 121)

N.J. SPECIFICATION NO. BME-TS-CABLE – EFFECTIVE DATE:  July 1, 2008

The New Jersey Department of Transportation, Bureau of Maintenance Engineering Specification for Traffic Signal Cable.

It is the purpose of this specification to describe minimum acceptable design requirements for multi- conductor traffic signal cable.

TYPE A

GENERAL – 1

1-1	The Traffic Signal Cable shall consist of THHN/THWN conductors twisted and covered with a polyvinyl chloride outer jacket. The Traffic Signal Cable shall conform to UL subject 1277. The cable shall be rated for 600 volts.

1-2	The conductor shall be bare, soft annealed copper wire, seven wire (Class B) stranding conforming to ASTM B 3 and B 8.

1-3	The insulation shall be high dielectric polyvinyl chloride covered with an insulation armor of nylon conforming to UL 83 for type THHN/THWN insulation. The insulated conductors shall be twisted and covered with helically applied suitable binding tape.

1-4	Circuit Identification: Insulation is colored and ink printed with conductor  number and colors per ICEA S-66-524, Appendix K-Table K-1 Method 3.

	CONDUCTOR. NUMBER
	BASE COLOR
	PRINTING

	  1.
	Black
	  1-Black

	  2.
	White
	  2-White

	  3.
	Red
	  3-Red

	  4.
	Green
	  4-Green

	  5.
	Orange
	  5-Orange

	  6.
	Blue
	  6-Blue

	  7.
	White
	  7-White-Black

	  8.
	Red
	  8-Red-Black

	  9.
	Green
	  9-Green-Black

	10.
	Orange
	10-Orange-Black

	11.
	Blue
	11-Blue-Black

	12.
	Black
	12-Black-White

	13.
	Red
	13-Red-White

	14.
	Green
	14-Green-White



Surface Printing:  Ink Printed, “14 AWG No.  Conductors – THHN/THWN– NJDOT EE Approval number – Company name and number.

[bookmark: _Toc161140902]4.27    PURCHASED MATERIAL
The following applies only to material awarded under the Contract:

1.	Only pre-approved cable with an EE number shall be allowed.

2.	The following amount of cable shall be procured and stored at the Contractors facility:

LF = Linear Feet

	A. 2/C
	25,000 LF

	B. 5/C
	20,000 LF

	C. 7/C
	20,000 LF

	D. 10/C
	20,000 LF

	E. 14/C
	20,000 LF



3.	The cable shall be supplied in 2,500 LF lengths on wooden reels.

4.	As the State purchases the cable, that cable amount shall be deducted from the quantity amount.

5.	At the end of the contract period the remaining cable shall be purchased by the State.

6.	The State may purchase any quantity over and above the minimum guaranteed amounts, provided that all minimum shipments are met. The State does not guarantee any amounts more than those listed in Section 2 above.

7.	The price of the cable shall include storage and delivery charges. Delivery shall be as per Bid Solicitation shipping instructions.

8.	The Contractor shall deliver all material within sixteen (16) weeks of the Contractor’s receipt of a purchase order from the Using Agency.

[bookmark: _Toc161140903]4.28    SPECIFICATIONS FOR LED SIGNAL INDICATIONS AND WARNING DEVICES

[bookmark: _Toc161140904]N.J. SPECIFICATION NO. BMEO-LED-H/M-PSH  (PRICE LINE 122) – EFFECTIVE DATE:  September 16, 2014

The purpose of this specification is to describe minimum performance/acceptable requirements for a LED (Light Emitting Diode) “walking person” and “hand” pedestrian signal head. The LED pedestrian signal head shall conform to the following:

CONSTRUCTION

A. The body section of the pedestrian signal head shall be a polycarbonate rectangular unit. The top and bottom portion shall be provided with positive locking and indexing rings integral with the body section. The integral locking rings shall consist of a single solid ring with 72 teeth and a minimum width of 1/4 inch. Openings in the rings shall accommodate 1-1/2 inch standard pipe nipples. The body shall be highway yellow matching to Fed-Std- 595b color #13538.

B. The door shall be a polycarbonate rectangular unit. The frame shall be gasketed to insure a dust and moisture free environment. The door/visor and ray director shall have a dull non-reflective black finish. Hinge pin and wing nut assemblies shall be stainless steel.

C. The LED module shall be gasketed and shall be installed in the door section of the pedestrian signal head.

D. The LED module shall display the appropriate symbols for a solid hand and a solid man. AILNGAP (aluminum indium gallium phosphorus), Portland orange (amber hand) LEDs shall be utilized. The substrate material may be either transparent or absorbing.  The white LEDs shall be lunar white (white man).

E. The housing size shall be 16 inches x 18 inches.

F. The lens shall be smooth surface, frosted (to prevent sun phantom) ultraviolet stabilized material. If polycarbonate material is used, the lenses must have a protective coating for scratch resistance.

G. Maintenance and/or replace of components shall be done using standard tools. All screws, washers, nuts and bolts shall be stainless steel.

H. The colors of the led module shall conform to chromaticity requirements of Section 8.04 and figure 1 of the VTCSH (Vehicle Traffic Control Signal Heads) standard.

[bookmark: _Toc161140905]N.J. SPECIFICATION NO. BMEO-LED-H/M-PSM  (PRICE LINE 123) – EFFECTIVE DATE:  September 16, 2014

The purpose of this specification is to describe minimum performance/acceptable requirements for a LED (Light Emitting Diode) “walking person” and “hand” pedestrian signal module.  The LED pedestrian signal module shall conform to the following:

CONSTRUCTION

A. The LED module shall replace the reflector, socket, gasket and lens assembly of the incandescent signal indication as specified in current New Jersey Department of Transportation Specification EB-PS-1 "Specification for Adjustable Face Pedestrian Signal Heads Incandescent Type Legend – Walk – Don’t Walk.”

B. The LED module shall be watertight when properly mounted in the traffic signal housing and shall not allow the ingress of water into any section of the traffic signal assembly. A continuous soft rubber or silicone gasket completely surrounding the unit shall be provided with each unit.

C. The LEDs and required circuit components shall be encased in a rigid housing for protection in shipping, handling and installation.

D. The LED module shall display the appropriate symbols for a solid hand and a solid man.  AlInGaP (Aluminum Indium Gallium Phosphorus), Portland Orange (amber hand) LEDs shall be utilized. The substrate material maybe either transparent or absorbing.  The white LED’s shall be lunar white (white man).

E. The LED module shall fit in a housing size of 16 inches x 18 inches.

F. The lens shall be smooth surface, frosted (to prevent sun phantom) ultraviolet stabilized material. If polycarbonate material is used, the lenses must have a protective coating for scratch resistance.

[bookmark: _Toc161140906]N.J. SPECIFICATION NO. BMEO-OP-RAG  (PRICE LINES 124 THROUGH 126) – EFFECTIVE DATE:  January 16, 2014

The purpose of these specifications is to describe minimum acceptable requirements for a Red, Amber, Green LED (Light Emitting Diode) modules for Optically Programmed Traffic Signal. The LED module shall conform to the following:

MIL-STD-810F for blowing rain.
Turn-on/Turn-off Time = 75 msec max. Total Harmonic Distortion <20%.



CONSTRUCTION

A. The LED module shall be a direct retrofit replacement for the lamp assembly of the optically programmed signal indication as specified in the current New Jersey Department  of Transportation Specification EB-TS-2, "Specifications for Optically Programmed Adjustable Face Vehicle Traffic Control Signal Heads.”

B. The LED's and required circuit components shall be encases in a rigid housing for protection in shipping, handling and installation.

C. The lens shall be ultraviolet stabilized material. The lens color shall be clear or uniformly tinted, provided the tinting does not affect the intensity or chromaticity. If polycarbonate material is used, the lenses must have a protective coating for scratch resistance.

D. Indium Gallium Nitride LED's (green) and Aluminum Indium Gallium Phosphorus LEDs (red and amber) shall be utilized.

ELECTRICAL

A. The module shall be capable to be connected by using straight spade connectors.

[bookmark: _Toc161140907]N.J. SPECIFICATION NO. BMEO-LED-SFB  (PRICE LINE 127) – EFFECTIVE DATE:  September 16, 2014

It is the purpose of this specification to describe minimum acceptable requirements for an Amber Solar Flashing Beacon Assembly.

A. Manual on Uniform Traffic Control Devices (MUTCD).

B. The current specification of the Institute of Transportation Engineering (ITE) standard titled Vehicle Traffic Control Signal Heads – Part 2: Light Emitting Diode (LED) Vehicle Traffic Signal Modules (VTCSH Part 2).

C. FCC Title 47, Subpart B, Section 15 on the Emission of Electronic Noise.

D. The solar flashing beacon assembly shall include 2 signal heads with visors, solar panels, batteries, 2 Amber LEDs, as requested, mounting brackets and electronic controls.

Upon written request, the Contractor shall provide certification, which includes a copy of the test report by an independent technical laboratory as to the module compliance with ITE specifications.   The certification shall also indicate that the tests were performed only after the modules received a 30 minute operational warm-up period immediately preceding the tests.  The Contractor shall have 5 business days to comply with this request.

CONSTRUCTION

A. The color of the complete assembly shall be highway yellow matching to  FED-STD-595B color #13538.  The beacon housing shall be polycarbonate and be available in 8 inch or 12 inch.

B. The beacon housing, 12 inch shall not weigh more than 40 pounds respectively.

C. The LED module shall be watertight when properly mounted in the beacon housing and shall not allow the ingress of water into any section of the traffic signal assembly. A continuous soft rubber or silicone gasket completely surrounding the unit shall be provided with each unit.

D. The beam color, beam intensity, and radiation pattern shall conform to the requirements for maintained minimum luminous intensity for LED signal modules and chromaticity as specified in the ITE (VTCSH, PART 2) standards.

E. All screws, washers, nuts and bolts shall be stainless steel. All components shall be readily accessible when the door is opened. Maintenance and/or replacement of components shall be done using standard tools

ELECTRICAL

A. The assembly shall be solar powered and not require any external power source to operate.

B. The 12 inch LED module shall consume no more than 7 watts respectively.

C. The LEDs shall operate over the temperature range of -40° F to +165° F.

D. The Unit shall operate for 30 days without any solar charging.

E. The batteries shall operate for at least three years. The assembly shall include dimming circuits to maintain battery charge.

[bookmark: _Toc161140908]N.J. SPECIFICATION NO. BMEO-TSH-AL (PRICE LINE 128) – EFFECTIVE DATE:  January 16, 2014

The purpose of these specifications is to describe minimum performance/acceptable requirements for an Adjustable Face Vehicle Traffic Control Aluminum Signal Head (HOUSING ONLY). The Adjustable face vehicle traffic control aluminum signal head (housing only) shall conform to the following:

The Traffic Signal Head shall consist of Three (3) – 12 inch sections; Manual on Uniform Traffic Control Devices (MUTCD); Adjustable Face Vehicle Traffic Control Head Standard Institute of Transportation Engineers (ITE); and

Standard Publication No. TS 1 National Electrical Manufacturer's Association (NEMA).
Standards and Publications - NEMA
https://www.nema.org

CONSTRUCTION

Construction shall conform to the following:

A. Traffic signal heads shall allow the installation of LED modules without any modification to the signal head.

B. Traffic signal heads shall be a combination of 12 inch signal sections as specified on the contract documents (or bid documents).

C. The main body assembly of the signal face shall be of enclosed sectional construction. The sections shall be made of high grade die-cast silicon aluminum alloy. All sections shall be identical and interchangeable with each other and shall be so designed that they interlock with each other forming a weatherproof assembly. Hinges or lugs shall be located inside each section for attaching the reflector assembly.

D. The housing door of each section shall be die-cast of silicon aluminum with an opening of sufficient diameter to accommodate the lens. On one side of the door, at top and bottom, there shall be a hinge so as to insure perfect alignment of the door. On the opposite side of the door, there shall be a wingnut assembly locking device to insure even gasket pressure. Twelve inch signal sections shall be secured with two wingnut assemblies. Hinge pins and locking device shall be stainless steel.

E. The entire signal section, with the exception of the inside surface of the visor, shall be finished with one coat of primer and one of enamel baked after application.  The color shall be highway yellow matching to FED-STD-595B color #13538. The inside surface of the visor shall be a dull non-reflective black.

F. The top and bottom of the die-cast section shall be provided with positive interlocking and indexing ring integral with the section. The integral locking ring shall consist of a single solid or double ring with 72 teeth and a minimum width of 1/4 inch. Openings in top and bottom of the section(s) shall accommodate 1-1/2 inch standard pipe nipples.

G. The signal section shall be dust-tight and shall consist of one lens, lamp, reflector and housing.  The distribution and intensity of the light, produced by the entire signal section shall conform to the requirements of Technical Report No. 1 of ITE.

H. The aluminum visors shall be twist or screw-on type and shall be 10 inches long, tunnel type for the 12 inch heads.  The visor shall be tilted downward 7 degrees from horizontal.

I. All screws, washers, nuts and bolts shall be stainless steel. All components shall be readily accessible when the door is opened. Maintenance and/or replacement of components shall be done using standard tools.

ELECTRICAL

Electrical shall conform to the following:

A. Each signal head shall be equipped with a barrier-type terminal block providing separate screws for each signal section and neutral wires. For all multi section signal heads, the terminal block shall be installed in the section with the yellow module. Each signal section shall be wired complete to the terminal block with color coded using spade lugs.

GENERAL FASTENERS

The Contractor shall assure all bolts, washers, nuts and screws shall be stainless steel as per NJDOT 2007 Standard Electrical Details.

TESTING

Upon the Using Agency’s request, the Contractor shall submit certification that all LED signal indications are not affected by any radio transmissions at any frequency (UHF, VHF, low bank, high band or 800 Mllz).  If the LED unit is affected by radio transmissions the product will be considered in non-compliance with these specifications and shall be rejected.

[bookmark: _Toc161140909]4.29    LED SIGNAL INDICATION AND WARNING DEVICES CATALOGS AND LITERATURE
Upon request, the Contractor shall furnish to the NJDOT or any Using Agency, manufacturer's catalogs and descriptive literature and specifications and shall also furnish related, supplementary information as often as requested during the term of the Contract at no additional cost.

[bookmark: _Toc161140910]4.30    LED SIGNAL INDICATION AND WARNING DEVICES EQUIPMENT QUALITY
All equipment supplied must be new and of the latest design.  The model must be in current production.  Discontinued models will not be accepted.

Each Unit delivered shall be completely assembled, thoroughly serviced, and ready for use when delivered to the Using Agency. Items specified in this Bid Solicitation must meet all specified standards, performance capabilities, and pertinent State and Federal codes and regulations.

[bookmark: _Toc161140911]4.31    LED SIGNAL INDICATION AND WARNING DEVICES PACKAGING AND SHIPPING
Packaging for shipment shall be such as to protect the product adequately to insure safe shipment.  Shipping cases shall be marked to show the name of the Contractor, name and address of the Using Agency, and the purchase order number.

The Contractor shall be required to protect all material so that it is delivered to the Using Agency in a first-class, undamaged condition. The Using Agency reserves the right to reject any material which is damaged or in any otherwise unacceptable condition. Any charges incurred due to unacceptable delivery will be the full responsibility of the Contractor.

[bookmark: _Toc161140912]4.32    LED SIGNAL INDICATION AND WARNING DEVICES INSTALLATIONS
No installation of any kind is required for LED signal indication and warning devices under this procurement.

[bookmark: _Toc161140913]4.33    LED SIGNAL INDICATION AND WARNING DEVICES PAYMENT

The Contractor supplying products to this Contract must be a registered participant and have the base part numbers listed on the Intertek-ETL LED Traffic Signal Modules Certification Program approved products website.  This requirement applies to Price Lines 122 and 123 only, and only the LED not the housing or other parts.  Only LED module would be on the list. 
Applicable provisions of the current specification of the Institute of Transportation Engineering (ITE} standard titled vehicle traffic control signal heads - Part 2: Light Emitting Diode (LED) Pedestrian Traffic Control Signal Indications (PTCSI part 2) Version adopted March 19, 2004.

Applicable provisions of the current specification of the Institute of Transportation Engineering (ITE) standard titled Vehicle Traffic Control Signal Heads: Light Emitting Diode (LED) Circular Signal Supplement dated June 27, 2005.

Applicable provisions of the current specification of the Institute of Transportation Engineering (ITE) standard titled vehicle Traffic Control Signal Heads - Part 2: Light Emitting Diode (LED) Vehicle Traffic Signal Modules (VTCSH Part 2).

The manufactured date of the LED shall be affixed to the back of the Unit.  The date shall be in calendar form with the month, day and full calendar year clearly displayed with letters and numbers or numbers only.

Manual on Uniform Traffic Control Devices (MUTCD); FCC Title 47, Subpart B, section 15 regulations for electrical noise.

	LED SIGNAL INDICATIONS AND WARNING DEVICES

	Descriptions
	Specification Number
Specification Date
Delivery Schedule/Time Frame

	Hand/Man Pedestrian Signal Head
	BMEO-LED-H/M-PSH Dated 09/16/2014

	Hand/Man Pedestrian Signal Module
	BMEO-LED-H/M-PSM Dated 09/16/2014

	Red, Amber, Green LED (Light Emitting Diode) modules for Optically Programmed Traffic Signal
	BMEO-OP-RAG Dated 01/16/2014

	Amber or (Light Emitting Diode) Solar Flashing Beacon Assembly
	BMEO-LED-SFB Dated 09/16/2014

	Adjustable Face Vehicle Traffic Control Aluminum Signal Head (Housing Only 3-12”) Sections
	BMEO-TSH-AL Dated 01/16/2016

	Lighting Poles Arms, Bases Black Lighting Arm Assembly
	DOT Sketch #12

	General Fasteners
	Delivery Schedule “A” – 16 weeks



[bookmark: _Toc161140914]4.34    SPECIFICATION FOR A GENERATOR AUXILIARY CABINET (GAC) – ALPHA  (PRICE LINE 130)
N.J. SPECIFICATION NO. BOSE-GAC-ALPHA– EFFECTIVE DATE:   January 24, 2024
The New Jersey Department of Transportation, Bureau of Operations Support & Engineering Specification for a Generator Auxiliary Cabinet – Alpha.
The purpose of this specification is to describe minimum performance/acceptable requirements for a Generator Auxiliary Cabinet – Alpha.
[bookmark: _Toc162147260][bookmark: _Toc196547779][bookmark: _Toc229470610][bookmark: _Toc259094044][bookmark: _Toc161140915][bookmark: _Toc129050062]4.34.1   GENERAL 
The Generator Auxiliary Cabinet – Alpha shall conform to the following:
[bookmark: _Toc162147261][bookmark: _Toc196547780][bookmark: _Toc229470611][bookmark: _Toc259094045][bookmark: _Toc161140916][bookmark: _Toc129050063]4.34.2    CONSTRUCTION 

	A.
	The GAC shall be constructed from 5052-H32 sheet aluminum alloy with a thickness of .125 inch. All inside and outside edges of the cabinet shall be free of burrs. The outside surface of the cabinet shall have a smooth, uniform, natural aluminum finish and shall match the Traffic Signal Controller (TSC) Cabinet. The finish shall be commercially smooth, substantially free of flow lines, and other defects that would impair serviceability or detract from general appearance. The cabinet shall include two battery shelves and a 19” equipment rack.


	B.
	GAC shall be NEMA 3R rated.   The dimensions for the GAC shall not exceed 50 inches in height, 20 inches in width and 20 inches in depth, and must not weigh more than 100 pounds when empty and must not weigh more than 500 pounds when fully populated as intended.  The GAC must house all the required equipment.


	C.
	The main door of the GAC must utilize a Corbin #2 key and the generator access panel on the GAC must be accessible using a standard NJDOT skeleton key used for meter cabinets.


	D.
	The main door opening shall be double flanged on all four (4) sides to keep dirt and liquids from entering the enclosure when door is opened. The main door shall be furnished with a gasket that satisfies the physical properties as found in UL508 table 21.1 and shall form a weathertight seal between the cabinet and door. The door hinges shall be stainless steel and continuous. The hinge pin shall be capped top and bottom by weld to render it tamperproof.  Door latching handle shall have a provision for padlocking in the closed position. The latching handles shall have provision for padlocking in the closed position. Each handle shall be 0.75 inch minimum diameter stainless steel with a minimum 0.5 inch shank.


	E.
	Door switches for each door and a temperature sensor for door status and cabinet temperature monitoring must be installed.


	F.
	The GAC cabinet must be ventilated and include a filter and thermostatically controlled fan.


	G.
	Full generator bypass components with an internal means of disconnect for the generator plug cord from the input plug shall be provided.


	H. 
	A “U” shaped stainless steel security bolt or heavy duty handle/fastener must be provided on the same side of the generator door at the lower side of controller cabinet to secure a chain to deter theft of a generator when in use.


	I.
	A "battery backup power-on" LED indicator light must be installed on the exterior of the cabinet as directed.  The LED must be wired in the ‘ON’ state until the Unit goes to auxiliary power, then turns off.


	J.
	The UPS unit must be rack-mounted in the cabinet.  The battery packs must be installed on shelves that are designed for that purpose.  The cabinet shall include a recessed external NEMA L5-30 male input plug in a lockable door constructed of the same material as the cabinet.



[bookmark: _Toc161140917]4.34.3    Uninterrupted power supply (ups)

A. The UPS shall be manufactured from Alpha and be at least 1,000 watt minimum with 1,400 VA.  The UPS shall conform to the following:
B. UPS shall be 19” rack mountable.
C. Batteries shall be sized to provide a minimum 3-hour operating runtime at full load.
D. Input Voltage: 120 VAC +12%, -29% (without Battery Discharge).
E. Output Voltage: 120 VAC +3%
F. UPS shall be rated for 1400 VA, 1000 Watt, minimum.
G. UPS shall be on-line double-conversion type.
H. Total Harmonic Distortion: 4.0% Max
I. Overload: 110% for 10 seconds, 200% for 0.05 second.
J. Operating temperature: -40°F to +165°F.
K. Relative Humidity: 5 to 95% (Non-condensing)
L. Communication: Standard serial interface for EIA 232. Option for NTCIP and TCP/IP via RJ45 connector to monitor UPS and receive alarms.
M. Furnish and install software as required to monitor the status of the UPS. Monitor parameter at a minimum shall include status of the UPS, Battery, and Alarms.
N. Contact closures for Power Up, Power Down, On Battery, Low Battery, and Alarms. 
O. Batteries shall operate from -40°F to +165°F and shall be sealed, maintenance free.
P. the UPS unit is capable of running a complete signalized intersection with a minimum 700 watt continuous load, and the unit provides a minimum of 1000 watt output capacity.
Q. the UPS includes 12 volt batteries wired in series supplying the necessary voltage and minimum wattage load of the UPS. Ensure that batteries are easily replaced and have a minimum of 50 AH and commercially available
R. Ensure that the Unit is designed for outdoor traffic signal applications, in accordance with the latest NEMA specifications.
S. The UPS Unit provides full power conditioning, filtering and surge protection

[bookmark: _Toc161140918]4.35   SPECIFICATION FOR A GENERATOR AUXILIARY CABINET (GAC) – OTHER  (PRICE LINE 131)
N.J. SPECIFICATION NO. BOSE-GAC-OTHER – EFFECTIVE DATE:  January 24, 2024
The New Jersey Department of Transportation, Bureau of Operations Support & Engineering Specification for a Generator Auxiliary Cabinet – Other.
The purpose of this specification is to describe minimum performance/acceptable requirements for a Generator Auxiliary Cabinet – Other.
[bookmark: _Toc161140919]4.35.1    GENERAL 
The Generator Auxiliary Cabinet shall conform to the following:
[bookmark: _Toc161140920]4.35.2    CONSTRUCTION 

	A.
	The GAC shall be constructed from 5052-H32 sheet aluminum alloy with a thickness of .125 inch. All inside and outside edges of the cabinet shall be free of burrs. The outside surface of the cabinet shall have a smooth, uniform, natural aluminum finish and shall match the Traffic Signal Controller (TSC) Cabinet. The finish shall be commercially smooth, substantially free of flow lines, and other defects that would impair serviceability or detract from general appearance. The cabinet shall include two battery shelves and a 19” equipment rack.


	B.
	GAC shall be NEMA 3R rated.   The dimensions for the GAC shall not exceed 50 inches in height, 20 inches in width and 20 inches in depth, and must not weigh more than 100 pounds when empty and must not weigh more than 500 pounds when fully populated as intended.  The GAC must house all the required equipment.


	C.
	The main door of the GAC must utilize a Corbin #2 key and the generator access panel on the GAC must be accessible using a standard NJDOT skeleton key used for meter cabinets.


	D.
	The main door opening shall be double flanged on all four (4) sides to keep dirt and liquids from entering the enclosure when door is opened. The main door shall be furnished with a gasket that satisfies the physical properties as found in UL508 table 21.1 and shall form a weathertight seal between the cabinet and door. The door hinges shall be stainless steel and continuous. The hinge pin shall be capped top and bottom by weld to render it tamperproof.  Door latching handle shall have a provision for padlocking in the closed position. The latching handles shall have provision for padlocking in the closed position. Each handle shall be 0.75 inch minimum diameter stainless steel with a minimum 0.5 inch shank.


	E.
	Door switches for each door and a temperature sensor for door status and cabinet temperature monitoring must be installed.


	F.
	The GAC cabinet must be ventilated and include a filter and thermostatically controlled fan.


	G.
	Full generator bypass components with an internal means of disconnect for the generator plug cord from the input plug shall be provided.


	H. 
	A “U” shaped stainless steel security bolt or heavy duty handle/fastener must be provided on the same side of the generator door at the lower side of controller cabinet to secure a chain to deter theft of a generator when in use.


	I.
	A "battery backup power-on" LED indicator light must be installed on the exterior of the cabinet as directed.  The LED must be wired in the ‘ON’ state until the Unit goes to auxiliary power, then turns off.


	J.
	The UPS unit must be rack-mounted in the cabinet.  The battery packs must be installed on shelves that are designed for that purpose.  The cabinet shall include a recessed external NEMA L5-30 male input plug in a lockable door constructed of the same material as the cabinet.



[bookmark: _Toc161140921]4.35.3    Uninterrupted power supply (ups)

A. The UPS shall be at least 1,000 watt minimum with 1,400VA.  The UPS shall conform to the following:
B. UPS shall be 19” rack mountable.
C. Batteries shall be sized to provide a minimum 3-hour operating runtime at full load.
D. Input Voltage: 120 VAC +12%, -29% (without Battery Discharge).
E. Output Voltage: 120 VAC +3%
F. UPS shall be rated for 1400 VA, 1000 Watt, minimum.
G. UPS shall be on-line double-conversion type.
H. Total Harmonic Distortion: 4.0% Max
I. Overload: 110% for 10 seconds, 200% for 0.05 second.
J. Operating temperature: -40°F to +165°F.
K. Relative Humidity: 5 to 95% (Non-condensing)
L. Communication: Standard serial interface for EIA 232. Option for NTCIP and TCP/IP via RJ45 connector to monitor UPS and receive alarms.
M. Furnish and install software as required to monitor the status of the UPS. Monitor parameter at a minimum shall include status of the UPS, Battery, and Alarms.
N. Contact closures for Power Up, Power Down, On Battery, Low Battery, and Alarms. 
O. Batteries shall operate from -40°F to +165°F and shall be sealed, maintenance free.
P. the UPS unit is capable of running a complete signalized intersection with a minimum 700 watt continuous load, and the unit provides a minimum of 1000 watt output capacity.
Q. the UPS includes 12 volt batteries wired in series supplying the necessary voltage and minimum wattage load of the UPS. Ensure that batteries are easily replaced and have a minimum of 50 AH and commercially available
R. Ensure that the Unit is designed for outdoor traffic signal applications, in accordance with the latest NEMA specifications.
S. The UPS unit provides full power conditioning, filtering and surge protection.

[bookmark: _Toc161140922]4.36    RESERVED.

[bookmark: _Toc161140923]4.37   PRODUCT QUALITY
Wherever a brand name is used, it is meant to denote the minimum acceptable level of quality and performance. Any item supplied as an "equal" must be approved by the Procurement Bureau and the NJDOT.

[bookmark: _Toc161140924]4.38    PRODUCT INSPECITION
The State reserves the right to inspect the Unit either at the Contractor’s facility or require that the Unit be available for inspection at the Using Agency delivery site. If, during inspection it  becomes apparent that corrections or alterations must to be made to the Unit to comply with bid specifications, the Contractor shall make all corrections prior to delivery and at no additional expense to the State.

[bookmark: _Toc161140925]4.39    MATERIAL PROTECTION
The Contractor shall be required to protect all material so that it is delivered to the using agency in a first- class, undamaged condition.

The State reserves the right to reject any material which is damaged or in an otherwise unacceptable condition.  Any charges incurred due to unacceptable delivery will be the full responsibility of the Contractor.

[bookmark: _Toc161140926]4.40    INSTALLATION
No installation of any kinds is required for this procurement.

[bookmark: _Toc161140927]4.4.1    INSTRUCTION OF AGENCY PERSONNEL
Complete instructions on the usage and maintenance of each Unit and a demonstration on the operation of the Unit shall be given by the Contractor free of charge, at the Using Agency delivery site.

[bookmark: _Toc161140928]4.42    SERVICE/REPAIR MANUALS
The Contractor is to furnish one set of all applicable parts, service and/or operator’s manuals upon delivery of the equipment at no additional cost.

[bookmark: _Toc161140929]4.43    QUANTITIES
Quantities listed on the State-Supplied Price Sheet are estimated annual usage by the New Jersey Department of Transportation and minimum order quantities. The State-Supplied Price Sheet has fields for these quantities.

[bookmark: _Toc161140930]4.43.1    ESTIMATED ANNUAL USAGE QUANTITIES
Estimated quantities are based upon prior year’s usage and are provided for informational purposes only. The State will not be limited to any minim or maximum order on items containing estimated quantities and the State reserves the right to order that item in any quantity desired.

[bookmark: _Toc161140931]4.43.2    MINIMUM SHIPMENT ORDER QUANTITIES
Minimum shipment order quantities provide the Contractor with a guaranteed minimum order quantity for shipment to a single site. The number in parenthesis following the estimated annual usage quantity on the item list is the minimum shipment quantity.

[bookmark: _Toc161140932]4.44    DELIVERY
Delivery schedule for each item shall be as indicated on the price line item description and must be in compliance with the following timeframes:

Price line items with a delivery schedule "A" designation - the Contractor shall deliver all material within sixteen (16) weeks of the Contractor's receipt of a purchase order from the Using Agency.

Price line items with a delivery schedule "B" designation - the Contractor shall deliver all material within twenty-four (24) weeks of the Contractor's receipt of a purchase order from the Using Agency.

Price line items with a delivery schedule "C" designation - the Contractor shall deliver all materials within forty-eight (48) weeks of the Contractor's receipt of a purchase order from the Using Agency.

For Price Lines 117 through 121 – Traffic Signal Cables – Delivery of materials should be sixteen (16) weeks after receipt of a purchase order.

The Unit is to be completely assembled, serviced and ready for use upon delivery to the Using Agency.

Any parts, controls, materials or attachments, which are standard and/or necessary to form an efficient and complete working unit, as judged by the State, are to be furnished whether specifically mentioned herein or not.

The final inspection and acceptance of the Unit will be at the Using Agency.

The Contractor shall deliver the Unit(s) to the Using Agency between the hours of 8:00 a.m. and 3:30 p.m. on regularly scheduled agency workdays.  Deliveries outside of these hours shall not be accepted.  The Contractor must provide twenty-four (24) hours’ notice (one work day) prior to delivery.

Deliveries shall not be made on the following State observed holidays:
· New Year’s Day;
· Martin Luther King Jr. Day;
· Presidents Day;
· Good Friday;
· Memorial Day;
· Juneteenth;
· Independence Day;
· Labor Day;
· Columbus Day;
· Election Day;
· Veterans Day;
· Thanksgiving Day; and
· Christmas Day.

[bookmark: _Toc161140933]4.45    SPECIAL DELIVERY INSTRUCTIONS AND PENALTY
Failure to supply material within the specified delivery timeframes as stated above may result in the cancellation of the Contractor’s Contract for that item.  The Contractor may request a three-week delivery extension.  The extension request must be submitted by the Contractor in writing with justification to the following:

New Jersey Department of Transportation
1035 Parkway Avenue
Trenton, NJ 08625
Attention:  Mr. Dan Black

If the Contractor fails to deliver after the extension period, the using agency may recommend that the Contractor’s contract be cancelled for that item.

[bookmark: _Toc161140934]4.46    EQUIPMENT QUALITY
All Units supplied must be new and of the latest design.  The model must be in current production.  Discontinued models will not be accepted.

Each Unit delivered shall be completely assembled, thoroughly serviced and ready for use when delivered to the Using Agency.

[bookmark: _Toc161140935]4.47    NJDOT DELIVERY LOCATIONS AND INSTRUCITONS
Deliveries will only be accepted from 8:00am to 11:30am.  Each NJDOT location must be notified a minimum of one (1) day in advance of a delivery.  Failure of advance notification to the location could result in non-acceptance of the shipment.

Following are the delivery locations for all material, ordered by the NJDOT.

	Northern Region
	Central Region
	Southern Region

	Stanhope Electrical Bureau
Rd 2, Higlen Drive
Stanhope, NJ, 07874

	Regional Electrical Maintenance 
999 Parkway Avenue 
Building #20 
Trenton, NJ, 08625
 

	Regional Electrical
Rear Building, 2nd Floor
Route 70 & NJ Turnpike
Cherry Hill, NJ, 08034

	Mt. Arlington Electrical
200 Stierle Court
Mt. Arlington, NJ, 07856-1322

	Regional Electrical Maintenance 
2436 Paynters 
Manasquan, NJ, 08736


	Totowa Electrical
300 Minnisink Rd.
Totowa, NJ, 07512-1805
	Regional Electrical Maintenance
455 Route 202/206, 
Building # 1300/SO15
Bedminster, NJ, 07921


	Newark Electrical Bureau
602 Route 1 & 9 South
Newark, NJ, 07114




For all other Using Agencies:  Please follow the instructions listed within the purchase order.

[bookmark: _Toc161140936]4.48    GUARANTEE
Manufacturer's standard warranty is to be for a minimum of one (1) year parts and labor from the time of delivery to and acceptance by the State. This guarantee shall apply to all equipment purchases.  Bidder should enclose a copy of its standard warranty with its bid proposal.

[bookmark: _Toc161140937]4.49    WARRANTY REQUIREMENTS
All units shall carry the standard warranty and/or guarantee. This warranty and/or guarantee shall accompany the unit when delivered.

On items requiring them, the Contractor shall supply a complete shop repair manual, parts manual, service manual and operation’s manual at the time of delivery, at no additional cost. In addition, instructions for the operation of the unit shall be provided.

All repairs and replacements under the conditions stated above shall be at no charge for service and labor to the State of New Jersey.

If any item supplied fails to perform satisfactorily within the first 30 days, it shall be replaced by a new one of the same make and model. Temporary equipment shall be provided within 24 hours while replacement is being processed.

[bookmark: _Toc161140938]LED SIGNAL INDICATION AND WARNING DEVICES WARRANTY
The equipment is to be unconditionally warranted for a period of one year from the time of written acceptance by the state as being fully operational. During the warranty period the Contractor shall replace parts and render service within 48 hours at no additional cost to the State.

Manufacturer's standard warranty must adhere to the item specification(s). This warranty shall apply to all equipment purchases and standard warranties shall be provided with each piece of equipment delivered.

[bookmark: _Toc161140939]4.50    PAYMENT
Payment will be made as outlined in the State Standard Terms and Conditions and  will only be made when all items ordered within the Purchase Order are delivered.  No partial payments will be made.

[bookmark: _Toc52286723][bookmark: _Toc55483925][bookmark: _Toc161140940]4.51    REPLACEMENT OF UNSATISFACTORY PRODUCT
In the event the product delivered does not meet the approved product specifications or is damaged prior to or at the time of delivery, as determined by the Using Agency, the Contractor shall immediately remove and replace the unsatisfactory product, at no cost to the Using Agency. The timeframe for the replacement shall not exceed the delivery days ARO listed on the State-Supplied Price Sheet.  Failure to comply may result in the product being removed from the Contract and a similar product obtained from another Contractor with any additional costs assumed by the original Contractor.

[bookmark: _Toc29987585][bookmark: _Toc55483926][bookmark: _Toc161140941]4.52    SUBSTITUTION OF DISCONTINUED OR REFORMULATED PRODUCTS
The Contractor may offer a substitution for any product discontinued or reformulated by the manufacturer in its Contract.  The State may consider substituting the discontinued or reformulated model with a new model provided that the unit offered meets or exceeds the Contract specifications.  All substitutions must be approved by the State. 

The Contractor must notify the State immediately in writing to the Division’s assigned Procurement Specialist stating that an item has been discontinued or reformulated by the manufacturer along with supporting documentation from that manufacturer that the item has been discontinued or reformulated.  The Contractor must provide in its letter the discontinued or reformulated model number, model number of the new product being offered, detailed literature for the new product being offered, the price of the discontinued or reformulated item and the price of the product being offered as a replacement.  The State will not approve the substitution of a discontinued or reformulated item without all of the above information.

The replacement product should be offered to the State at that same price as the discontinued or reformulated product.

[bookmark: _Toc52286725][bookmark: _Toc55483927][bookmark: _Toc161140942]4.53    SUBSTITUTION OF PRODUCTS ON A TEMPORARY BASIS
A Contractor may offer a substitute product for the contracted product on a temporary basis provided that the specifications are met and the Contractor provides proper justification for the temporary substitution.  The justification provided to the Division by the Contractor must include a letter from the contracted brand manufacturer, stating that the product is not able to be offered, estimated duration of product unavailability and the reasoning for the unavailability of product. The request for temporary product substitution, with all supporting documentation, must be submitted to the Division for review and approval.  The substitute product must be offered to the State at the same or more favorable pricing. The Contractor cannot offer the substituted product until it is approved by the Division through a change order in NJSTART.  Once the originally contracted product is available again, the Contractor must immediately notify the Division in writing.  A temporary replacement of product is not meant as a permanent product replacement.  

[bookmark: _Toc161140943]4.54    PRICE LIST UPDATES
For Price Lines 140 through 154, a Contractor must only provide the products offered within the brand/price line awarded.  

The State reserves the right to redact all products which do not apply to the specific products/categories identified in this Bid Solicitation.

The Contractor may request a price list update for each contracted brand once during a rolling twelve (12) month period.  If a Contractor has been awarded more than one (1) brand/Price Line, each brand/price line may be updated at different times during a rolling twelve (12) month period, but in no event shall a Contractor update a single awarded brand more than one (1) time during a rolling twelve (12) month period.

Requests for price list updates shall be limited to the Price Line and brand that a Contractor is awarded.  The file name should contain the Contract number and date of the revised price list. The Contractor must provide the revised price list via email, in pdf or Excel format.  The correspondence to the Division with the revised price list shall reference the location of the specific price line that has been revised. The revised price list will not be considered valid until it has been reviewed and approved by the Procurement Bureau and published in NJSTART.

[bookmark: _Toc115337434][bookmark: _Toc140562712][bookmark: _Toc161140944]4.55    CONTRACT METHOD OF OPERATION
A Method of Operation, as may be amended from time to time, shall be posted by the Division of Purchase and Property upon award of the Contracts resulting from this Bid Solicitation. The Method of Operation will be posted to the “Attachments” Tab of the Contract’s NJSTART page. The Method of Operation applies to Using Agencies and MUST always be followed.

The Method of Operation will include an award summary which will identify Contractors for each brand/price line awarded.

For Price Lines 140 through 154 Only:

Using Agency shall initiate a Contract purchase on an as-needed basis by preparing clear and unambiguous requirements for the goods to be ordered, based solely upon the Using Agency’s needs.  
Using Agencies shall select a brand awarded that offers products suitable to meet the Using Agency’s project requirements.  Using Agencies shall solicit mini-bid responses from all Contractors awarded the brand selected.
Using Agencies are advised that multiple Contractors may be awarded the same brand.  As such, Using Agencies shall solicit mini-bid responses from all Contractors awarded the brand required.  The Using Agency shall establish the date and time for all Contractors to respond to the mini-bid request and inform all Contractors of the same.  All selected Contractors shall respond to the mini-bid request with a pricing response or a “no bid” response.   In response to a request for a mini-bid, Contractors may provide better pricing to the Using Agency than that submitted on the price sheet. 
The Using Agency shall utilize the Contractor offering the lowest price for the brand/product required. The Using Agency may bypass the Contractor offering the lowest price for the product required only when that Contractor is not able to provide the requested product, when the Contractor cannot meet its contracted delivery commitment. 
At the time of auditing, the Using Agency will be required to demonstrate that the establishment of the purchase requirements is free from any bias or inclination against or in favor of any Contractor.  Using its purchase requirements, current price list and Contract discount or markup, the Using Agency shall determine the final purchase price for each Contract price line item. The Using Agency must document all phases of its Contract selection process for each purchase under any Contract resulting from this Bid Solicitation.  






[bookmark: _Toc161140945]GENERAL CONTRACT TERMS
The Contractor shall have sole responsibility for the complete effort specified in this Contract.  Payment will be made only to the Contractor or to the authorized dealers/distributors, if applicable.  The Contractor is responsible for the professional quality, technical accuracy and timely completion and submission of all deliverables, services or commodities required to be provided under this Contract.  The Contractor shall, without additional compensation, correct or revise any errors, omissions, or other deficiencies in its deliverables and other services.  The approval of deliverables furnished under this Contract shall not in any way relieve the Contractor of responsibility for the technical adequacy of its work.  The review, approval, acceptance or payment for any of the deliverables, goods or services, shall not be construed as a waiver of any rights that the State may have arising out of the Contractor’s performance of this Contract.

[bookmark: _Toc161140946]5.1    CONTRACT TERM AND EXTENSION OPTION
The base term of this Contract shall be for a period of three (3) years.  The anticipated Contract effective date is provided on the “Summary” page of the Bid Solicitation in NJSTART.  If delays in the procurement process result in a change to the anticipated Contract effective date, the Contractor agrees to accept a Contract for the full term of this Contract. 

This Contract may be extended up to three (3) years with no single extension exceeding one (1) year, by the mutual written consent of the Contractor and the Director at the same terms, conditions, and pricing at the rates in effect in the last year of this Contract or rates more favorable to the State.  

[bookmark: _Toc400531508][bookmark: _Toc428533979][bookmark: _Toc32310704][bookmark: _Toc161140947]5.2    CONTRACT TRANSITION
In the event that a new Contract has not been awarded prior to the expiration date for this Contract, including any extensions exercised, and the State exercises this Contract transition, the Contractor shall continue this Contract under the same terms, conditions, and pricing until a new Contract can be completely operational.  At no time shall this transition period extend more than 180 calendar days beyond the expiration date of this Contract, including any extensions exercised.

[bookmark: _Toc118513795][bookmark: _Toc400531563][bookmark: _Toc428534035][bookmark: _Toc32310758][bookmark: _Toc161140948][bookmark: OLE_LINK3][bookmark: OLE_LINK4]5.3    PERFORMANCE SECURITY
Not applicable to this procurement.

[bookmark: _Toc400531513][bookmark: _Toc428533984][bookmark: _Toc32310709][bookmark: _Toc161140949]5.4    OWNERSHIP OF MATERIAL
Not applicable to this procurement.

[bookmark: _Toc161140950]5.5    SUBSTITUTION OF STAFF
Not applicable to this procurement.

[bookmark: _Toc161140951]5.6    DELIVERY TIME AND COSTS
Unless otherwise noted in this Bid Solicitation or on the State-Supplied Price Sheet, all delivery times are:

Price line items with a delivery schedule "A" designation - the Contractor shall deliver all material within sixteen (16) weeks of the Contractor's receipt of a purchase order from the Using Agency.

Price line items with a delivery schedule "B" designation - the Contractor shall deliver all material within twenty-four (24) weeks of the Contractor's receipt of a purchase order from the Using Agency.

Price line items with a delivery schedule "C" designation - the Contractor shall deliver all materials within forty-eight (48) weeks of the Contractor's receipt of a purchase order from the Using Agency.

For Price Lines 117 through 121 – Traffic Signal Cables – Delivery of materials should be sixteen (16) weeks after receipt of a purchase order.

Prices for items in Quotes shall be submitted Freight On Board (F.O.B.).   The Contractor shall assume all costs, liability and responsibility for the delivery of merchandise in good condition to the State's Using Agency or designated purchaser.  The delivery days ARO/F.O.B. referenced above does not cover "spotting" but does include delivery on the receiving platform of the Using Agency at any destination in the State of New Jersey unless otherwise specified.  No additional charges will be allowed for any additional transportation costs resulting from partial shipments made at the Contractor’s convenience when a single shipment is ordered.  The weights and measures of the State's Using Agency receiving the shipment shall govern.  Collect on Delivery (C.O.D.) Terms are not permitted.


[bookmark: _Toc161140952]5.7    AUTHORIZED DEALERS AND/OR DISTRIBUTORS
The Contractor must provide a list of the Dealer(s)/Distributor(s) that will service the Contract.  The Contractor will be required to submit the following forms for each Dealer/Distributor, prior to the Dealer/Distributor being permitted to perform any work on the Contract:
A. Ownership Disclosure (N.J.S.A. 52:25-24.2);
B. Disclosure of Investment Activities in Iran (N.J.S.A. 52:32-55 et. seq.);
C. Disclosure of Investigations and Actions Involving Bidder Form;
D. MacBride Principles  (N.J.S.A. 52:34-12.2);
E. Source Disclosure Certification (N.J.S.A. 52:34-13.2);
F. Vendor Certification (P.L. 2005, c.271);
G. New Jersey Business Registration (N.J.S.A. 52:32-44);
H. Proof of insurance as specified herein;
I. Proof of compliance with New Jersey Affirmative Action requirements (N.J.A.C. 17:27-1.1 et. seq.):
· New Jersey Form AA-302 Affirmative Action Employee Information Report; or 
· New Jersey Affirmative Action Certificate; or 
· Federal Affirmative Action Approval Letter; and
J.	Certification of Non-Involvement of Prohibited Activities in Russia or Belarus Pursuant to P.L.2022, c.3	
A Contractor may submit a request to add or remove Dealers/Distributors at any time during the Contract term, including any extension(s) thereof.  Any such request should be emailed to the Procurement Specialist assigned to this procurement.

[bookmark: _Toc400531525][bookmark: _Toc428533996][bookmark: _Toc32310718][bookmark: _Toc161140953]5.8    LIQUIDATED DAMAGES
Not applicable to this procurement.

[bookmark: _Toc400531531][bookmark: _Toc428534002][bookmark: _Toc32310724][bookmark: _Toc161140954]5.9    RETAINAGE
Not applicable to this procurement.

[bookmark: _Toc161140955]5.10    ELECTRONIC PAYMENTS
With the award of this Contract, the successful Contractor(s) will be required to receive its payment(s) electronically.  In order to receive payments via automatic deposit from the State of New Jersey, the Contractor must complete the EFT information within its NJSTART Vendor Profile.  Please refer to the QRG entitled “Vendor Profile Management – Company Information and User Access” for instructions. 

[bookmark: _Toc161140956]5.11    PROCUREMENT EFFICIENCY PROGRAM
A. Quarterly Sales Reporting - The Contractor shall submit a Sales Report documenting all sales made under the Contract.  The Sales Report shall be submitted directly to Periscope no later than thirty (30) calendar days after the end of each calendar quarter. The calendar quarters will end March 31, June 30, September 30, and December 31. The Sales Report must contain the following information:  
· Complete and accurate details of all sales, credits, returns, refunds, and the like for the reporting quarter;
· Purchasing entity;
· Total of Procurement Efficiency Program Fee amount due for the reporting quarter;
· Such other information as the State may reasonably request;
· If no sales were made against this Contract during the reporting quarter, then a report shall be submitted showing zero sales and zero Procurement Efficiency Program Fee due; and
· Quarterly Sales Reporting and remittance of the Procurement Efficiency Program Fee shall begin on the first calendar quarter starting after the effective date of the Contract.
B. Procurement Efficiency Program Fee - For all purchases made under this Contract, that have been invoiced, the Contractor shall remit the Procurement Efficiency Program Fee in the amount of one percent (1%) of all Purchases to Periscope acting on behalf of the State of New Jersey. 
C. Remittance of the Procurement Efficiency Program Fee - On a quarterly basis, the Contractor shall remit the Procurement Efficiency Program Fee directly to Periscope no later than thirty (30) days after the end of each calendar quarter. The calendar quarters will end March 31, June 30, September 30, and December 31.  Failure to remit the Procurement Efficiency Program Fee timely and accurately may result in Contract termination as outlined in the “Termination of Contract” clause of the State of New Jersey Standard Terms and Conditions. 
D. NJSTART Marketplace Catalog Enablement - Contractor shall cooperate with State and/or Periscope as requested to upload catalog items and pricing consistent with this Contract. Contractor shall upload catalog within (thirty) 30 calendar days of the date of execution of this Contract. Failure to cooperate will result in the Contractor’s good and/or services not being represented in the NJSTART Marketplace. The Contractor shall ensure that the catalog complies with the scope, and terms and conditions of this Contract. Any identified deviation from the Contract must be corrected immediately. Any catalog that does not comply with the scope and terms and conditions of this Contract can lead to a breach of contract and will be escalated to the Division of Purchase and Property’s Contract Compliance and Audit Unit for review and possible action.  
E. Retention and Inspection of Records and Audit - The Contractor shall keep records of all sales made to all Using Agencies in sufficient detail to enable the State to determine the Procurement Efficiency Program Fee payable by the Contractor. The State and/or Periscope may examine and audit, at its own expense, Contractor’s sales records and Sales Reports for completeness and accuracy. If such examination reveals underpayment of the Procurement Efficiency Program Fee, the Contractor shall immediately pay to Periscope the amount of deficiency. If the examination reveals an underpayment of 5% or more, then the Contractor shall reimburse the State and/or Periscope for the cost of the audit. 




[bookmark: _Toc161140957]DATA SECURITY REQUIREMENTS – CONTRACTOR RESPONSIBILITY 
Not applicable to this procurement.

[bookmark: _4.4.1.1_Ownership_Disclosure][bookmark: _4.4.1.1_Signatory_page][bookmark: _4.4.2.3_Contract_Schedule][bookmark: _4.4.2.4_mobilization_and][bookmark: _Toc161140958]MODIFICATIONS TO THE STATE OF NEW JERSEY STANDARD TERMS AND CONDITIONS
Not applicable to this procurement.

[bookmark: _Toc161140959]QUOTE EVALUATION AND AWARD

[bookmark: _Toc400531542][bookmark: _Toc428534014][bookmark: _Toc32310736][bookmark: _Toc161140960]8.1    RIGHT TO WAIVE
Pursuant to N.J.A.C. 17:12-2.7(d) the Director may waive minor irregularities or omissions in a Quote.  The Director reserves the right to waive a requirement provided that the requirement does not materially affect the procurement or the State's interests associated with the procurement.
[bookmark: _Toc400531543][bookmark: _Toc428534015][bookmark: _Toc32310737]
[bookmark: _Toc161140961]8.2    DIRECTOR’S RIGHT TO ACCEPT OR REJECT A QUOTE
The Director reserves the right to reject any or all Quotes, or to award in whole or in part if deemed to be in the best interest of the State to do so. The Director shall have authority to award Contracts in accordance with N.J.S.A. 52:34-12. 

[bookmark: _Toc161140962]8.3    RECIPROCITY FOR JURISDICTIONAL BIDDER PREFERENCE
In accordance with N.J.S.A. 52:32-1.4 and N.J.A.C. 17:12-2.13, the State of New Jersey will invoke reciprocal action against an out-of-State Bidder whose state or locality maintains a preference practice for its in-state Bidders.  The State of New Jersey will use the annual surveys compiled by the Council of State Governments, National Association of State Procurement Officials, or the National Institute of Governmental Purchasing or a State’s statutes and regulations to identify States having preference laws, regulations, or practices and to invoke reciprocal actions. The State of New Jersey may obtain additional information as it deems appropriate to supplement the stated survey information.

A Bidder may submit information related to preference practices enacted for a State or Local entity outside the State of New Jersey. This information may be submitted in writing as part of the Quote response, including name of the locality having the preference practice, as well as identification of the county and state, and should include a copy of the appropriate documentation, i.e., resolution, regulation, law, notice to Bidder, etc.  It is the responsibility of the Bidder to provide documentation with the Quote or submit it to the Director within five (5) business days after the deadline for Quote submission.  Written evidence for a specific procurement that is not provided to the Director within five (5) business days of the public Quote submission date may not be considered in the evaluation of that procurement, but may be retained and considered in the evaluation of subsequent procurements.

[bookmark: _Toc400531545][bookmark: _Toc428534017][bookmark: _Toc32310739][bookmark: _Toc161140963]8.4    CLARIFICATION OF QUOTE
After the Quote Opening Date, unless requested by the State as noted below, Bidder contact with the Procurement Bureau regarding this Bid Solicitation and the submitted Quote is not permitted. 

After the Quotes are reviewed, one (1), some or all of the Bidders may be asked to clarify certain aspects of its Quote.  A request for clarification may be made in order to resolve minor ambiguities, irregularities, informalities or clerical errors.  Clarifications cannot correct any deficiencies, material omissions, or used to revise or modify a Quote.

The Director reserves the right to request that a Bidder to explain, in detail, how the Quote price was determined.

[bookmark: _Toc32310741][bookmark: _Toc161140964][bookmark: _Toc118513837][bookmark: _Toc400531547][bookmark: _Toc428534019]8.5    ORAL PRESENTATION 
Not applicable to this procurement.

[bookmark: _Toc161140965]8.6    TIE QUOTES
Tie Quotes will be awarded by the Director in accordance with N.J.A.C. 17:12-2.10. 

For the purposes of tie-breaking, any tie-break scenario shall be made utilizing the delivery schedule bid, followed by the criteria set forth in N.J.A.C. 17:12-2.10.  The delivery timeframe will be utilized in any tie-break scenario, and, in the case of a range of delivery days for the product bid, the highest day in the range will be used for the purposes of the tie-break.  For example, if a Bidder offers 10 - 20 days ARO for the product bid, the 20 days will be used for the basis of the tie-break. 

[bookmark: _Toc161140966]8.7    STATE'S RIGHT TO INSPECT BIDDER’S FACILITIES
The State reserves the right to inspect the Bidder’s establishment before making an award, for the purposes of ascertaining whether the Bidder has the necessary facilities for performing the Contract.

[bookmark: _Toc161140967]8.8    STATE'S RIGHT TO CHECK REFERENCES
The State may also consult with clients of the Bidder during the evaluation of Quotes. Such consultation is intended to assist the State in making a Contract award that is most advantageous to the State.

[bookmark: _Toc161140968]8.9    EVALUATION CRITERIA
The following evaluation criteria categories, not necessarily listed in order of significance, will be used to evaluate Quotes received in response to this Bid Solicitation.  The evaluation criteria categories may be used to develop more detailed evaluation criteria to be used in the evaluation process.

[bookmark: _Toc118513839][bookmark: _Toc400531549][bookmark: _Toc428534021][bookmark: _Toc32310743][bookmark: _Toc161140969]8.9.1  TECHNICAL EVALUATION CRITERIA
The following criteria will be used to evaluate Quotes received in response to this Bid Solicitation:  
A. The Bidder’s demonstration in the Quote that the Bidder understands and is able to complete the requirements of the Scope of Work as sought.

[bookmark: _Toc118513840][bookmark: _Toc400531550][bookmark: _Toc428534022][bookmark: _Toc32310744][bookmark: _Toc161140970]8.9.2  PRICE EVALUATION
For evaluation purposes, Bidders will be ranked from lowest to highest according to the sum of the Quote prices located on the State-Supplied Price Sheet accompanying this Bid Solicitation for the following groups:

	Price Line #
	
Description

	Group 1 - Price Lines 1 and 2

	1
	Traffic Signal Indication Parts Replacement Visors – 8 Inch, as per NJDOT Spec. # BME-TS-Visor, Dated April 28, 2010

	2
	Traffic Signal Indication Parts Replacement Visors – 12 Inch, as per NJDOT Spec. # BME-TS-Visor, Dated April 28, 2010

	Group 2 - Price Lines 5 and 6

	5
	Traffic Signal Indication Parts Traffic Signal Indication - 8 Inch (Housing Only) as per NJDOT Spec. Dated April 26, 2007 Drawing BME-TS-Head

	6
	Traffic Signal Indication Parts Traffic Signal Indication - 12 Inch (Housing Only) as per NJDOT Spec. No. BME-TS-Head Dated April 26, 2007

	Group 3 - Price Lines 9 and 10

	9
	Traffic Signal Indication/Parts 3M-R.A.G. (3 Section – 12 Inch) as per NJDOT Spec. Drawing EB-TS-2

	10
	Traffic Signal Indication/Parts 3M - Arrow  (1 Section) as per NJDOT Spec. Drawing EB-TS-2

	Group 4 - Price Lines 31 through 64

	31
	Traffic Signal Poles, Arms, Bases Paint Adder for Poles and Arms Only – Up to and including 23 feet in length 

	32
	Traffic Signal Poles, Arms, Bases Paint Adder for Poles and Arms Only – Over 23 feet in Length

	33
	Traffic Signal Pole & Lighting Pole Bases Paint Adder for Bases Only

	34
	Traffic Signal Hangers Brackets TB-20 Base 2007 Standard Electrical Details T-0207

	35
	Traffic Signal Hangers Brackets HHB Base 2007 Standard Electrical Details T-1507

	36
	Traffic Signal Hangers Brackets K Base 2007 Standard Electrical Details T-1007

	37
	Traffic Signal Hangers Brackets Traffic Signal Pole Type T-2007 Standard Electrical Details T-0107

	38
	Traffic Signal Hangers Brackets Traffic Signal Pole Type C 2007 Standard Electrical Details T-0807

	39
	Traffic Signal Hangers Brackets Traffic Signal Pole Type K 2007 Standard Electrical Details T -1007

	40
	Traffic Signal Hangers Brackets Pedestal Pole – 8 Foot 2007 Standard Electrical Details T-0707

	41
	Traffic Signal Hangers Brackets Pedestal Pole – 12 Foot 2007 Standard Electrical Details T-0707

	42
	Traffic Signal Hangers Brackets Traffic Signal Standard, Type KE 2007 Standard Electrical Details T -1007

	43
	Traffic Signal Pole, Type KE Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch #3 (Attachment #5)

	44
	Traffic Signal Poles, Arms, Bases Traffic Signal Pole Type K - Mounting Adapter for Mongoose Luminaire as per NJDOT Sketch #4 (Attachment #5)

	45
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – Trombone 15 ft. as per NJDOT Drawing T-1207

	46
		Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – Trombone 20 ft. as per NJDOT Drawing T-1207




	47
		Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm –15 ft. as per NJDOT Drawing T-0307




	48
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 20 ft. as per NJDOT Drawing T-0307

	49
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 25 ft. as per NJDOT Drawing T-0307

	50
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 15 ft. Type K as per NJDOT Drawing T-0907

	51
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 20 ft. – Type K as per NJDOT Drawing T-0907

	52
	Traffic Signal Poles, Arms, Bases Traffic Signal Mast Arm – 25 ft. – Type K as per NJDOT Drawing T-0907

	53
	Traffic Signal Poles, Arms, Bases Traffic Signal Standard Type T Pole Cap as per NJDOT Drawing T-0107

	54
	Traffic Signal Poles, Arms, Bases Traffic Signal Standard Type K Pole Cap as per NJDOT Drawing T-1007 Detail C

	55
	Paint Adder Poles, Arms, Lighting Poles, Arms

	56
	Lighting  Poles, Arms, Bases Lighting Pole,  Type L as per NJDOT Spec. Drawing P-0189

	57
	Lighting Poles, Arms, Bases Lighting  Pole, Type L-40 as per NJDOT Spec. Drawing P-0289

	58
	Lighting Poles, Arms, Bases Lighting Arm, 8 Foot as per NJDOT Spec. Drawing P-0389

	59
	Lighting Poles, Arms, Bases Lighting Arm, 15 Foot as per NJDOT Spec. Drawing P-0389

	60
	Lighting Poles, Arms, Bases Transformer Base (Lighting) as per NJDOT Spec. Drawing L-2107

	61
	Lighting Poles, Arms, Bases, Lighting Pole, 22 Foot Bridge Mounted Pole – Flagpoles Inc. #RTA8M22AABXV-HH, Arm In Line with Hand Hole 12 inches from Bottom with Vibration Dampener, Flagpoles #RTA8M22AABXV-HH  Only - NO SUBSTITUTIONS

	62
	Lighting Poles, Arms, Bases, Lighting Pole, 37 Foot Bridge Mounted Pole - Flagpoles Inc. #RTA8X37AABXV-HH, Arm In Line with Hand Hole 12 inches From Bottom with Vibration Dampener, Flagpoles #RTA8X37AABXV-HH Only - NO SUBSTITUTIONS

	63
	Lighting Poles, Arms, Bases Lighting Arm Assembly as per NJDOT Sketch #5 (Attachment #5)

	64
	Lighting Poles, Arm, Bases Mounting Adapter for Offset Luminaire as per NJDOT Drawing L -1807

	Group 5 - Price Lines 65 through 78

	65
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Standard Type S (Includes Anchorage) with Alternate Pole Top as per Bid Solicitation Specifications and NJDOT Detail T-1107 & T-4307 and Reference Sketch #3 and Sketch #4 (Attachment #5)

	66
		Steel Traffic Signal Poles and Arms Steel Traffic Signal Standard Type SC (Includes Anchorage) with Alternate 
Pole Top as per Bid Solicitation Specifications and NJDOT Detail T-1107 & T-4307 and Reference 
Sketch #3 and Sketch #4 (Attachment #5)




	67
	Traffic Signal Poles, Arms, Bases Steel Traffic Signal Arm - 20 ft. as per NJDOT Drawing T-1307

	68
	Traffic Signal Poles, Arms, Bases Steel Traffic Signal Arm - 25 ft. as per NJDOT Drawing T-1307

	69
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Arm - 30 ft. as per NJDOT Drawing T-1307

	70
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Arm- 35 ft. as per NJDOT Drawing T-1307

	71
	Steel Traffic Signal Poles and Arms, Bases Steel Traffic Signal Arm- 40 ft. as per NJDOT Drawing T-1307

	72
	Steel Traffic Signal Poles and  Arms, Bases Steel Traffic Signal Arm- 45 ft. as per NJDOT Drawing T-1307

	73
	Steel Traffic Signal Poles and Arms, Bases Steel Traffic Signal Arm- 50 ft. as per NJDOT Drawing T-1307

	74
	Steel Traffic Signal Poles and Arms, Steel Traffic Signal Standard, Type SC Lighting Arm - 15 ft., as per NJDOT Drawing T -1307

	75
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Standard, Type SC Lighting Arm - 20 ft., as per NJDOT  Drawing T-1307

	76
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Anchorages as per NJDOT Drawing T-4307

	77
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Type S - Mounting Adapter for Mongoose Luminaire, as per NJDOT Sketch #4 (Attachment #5)

	78
	Steel Traffic Signal Poles and Arms Steel Traffic Signal Type SC -Mounting Adapter for Mongoose Luminaire, as per NJDOT Sketch #4 (Attachment #5)

	Group 6 - Price Lines 79 through 88

	79
	Paint Adder Cabinet - Up to and Including 23 Feet in Length, as per Bid Solicitation Sections 4.7 and 4.23 for Cabinets and Cabinet Hardware

	80
	Paint Adder Cabinet - Over  23 Feet in Length, as Per Bid Solicitation Sections 4.7 and 4.23 Cabinets and Cabinet Hardware 

	81
	Cabinets and Cabinet Hardware Meter Cabinet, Type T As Per NJDOT Spec. Drawing P -0489, and NJDOT Drawing T-4307

	82
	Cabinets and Cabinet Hardware Meter Cabinet Type T (Sheet Metal), as per NJDOT Spec. Drawing T -3507

	83
	Cabinets and Cabinet Hardware Meter Cabinet, Fabricated Typed (53 Inch), as per NJDOT Sketch #11 (Attachment #5)

	84
	Cabinets and Cabinet Hardware Meter Cabinet Type M (Sheet Metal), as per NJDOT Spec. Drawing L -1407

	85
	Cabinets and Cabinet Hardware Cabinet Type P, as per NJDOT Sketch #6 (Attachment #5)

	86
	Cabinets and Cabinet Hardware Cabinet Type P Split Skirt, as per NJDOT Sketch #7 (Attachment #5)

	87
		Cabinets and Cabinet Hardware Cabinet, Type P Skirt, as per NJDOT Sketch #7 (Attachment #5)




	88
		Cabinets and Cabinet Hardware Meter Cabinet Type M  - Lock & Keys, as per NJDOT Spec. Drawing L -1407




	Group 7 - Price Lines 91 through 95

	91
	Signs/ Sign Brackets Sign – Red Signal Ahead – LED, as per NJDOT Spec. Drawing T -1407

	92
	Signs/Sign Brackets – Blankout Sign LED “No Left Turn”, as per NJDOT Drawing T-1407 & Sketch #10 (Attachment #5)

	93
	Signs/Sign Brackets – Blankout Sign LED “No Right Turn”, as per NJDOT Drawing T-1407 & Sketch #10 (Attachment #5)

	94
	Signs/Sign Brackets – Blankout Sign LED “No Turn On Red” 2007 Standard Electrical Detail T -1407, as per NJDOT Drawing T-1407,BME – LED-NTBLO Dated 5/31/2018 & NJDOT Sketch #10 (Attachment #5)

	95
	Signs/Sign Brackets – Blankout Sign LED “(Message To Be Determined When Ordering) 2007 Standard Electrical Detail T -1407, as per NJDOT Drawing T-1407, BME  LED-NTBLO Dated 5/31/2018 & Sketch #10 (Attachment #5)

	Group 8 - Price Lines 101 and 102

	101
	Miscellaneous Signal Products Devices, Wireless Transceiver System-2, Including All Mounting Hardware, Antennas, Connectors, Cables for a Complete System, as per NJDOT Spec. BME-WCCS, Dated 5/24/10

	102
	Miscellaneous Signal Products Devices, Wireless Transceiver System-3, Including All Mounting Hardware, Antennas, Connectors, Cables for a Complete System, as per NJDOT Spec. BME-WCCS, Dated 5/24/10

	Group 9 – Price Lines 103 and 104

	103
	Miscellaneous Signal Products Devices, Backplate – 8” Signal Head, as per NJDOT Drawing T-1807

	104
	Miscellaneous Signal Products Devices, Backplate – 12” Signal Head, as per NJDOT Drawing T-1807

	Group 10 - Price Lines 105 through 108

	105
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base TB-20, as per NJDOT Drawing T-0207

	106
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base K, as per NJDOT Drawing T-0707

	107
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base TB-30, as per NJDOT Drawing L-1507

	108
	Miscellaneous Signal Products Devices, Plastic Door Transformer Base TB-17, as per NJDOT Drawing L-2107

	Group 11 - Price Lines 109 through 111

	109 
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Econolite 5 Inch Border Aluminum, Black Non-Louvered 3 Section with 3 Inch 3M Tape Border - Econolite P43-01 Only - NO SUBSTITUTIONS

	110
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Econolite 5 Inch Border, Aluminum, Black Non-Louvered 4 Section with 3 Inch 3M Tape Border - Econolite P44-01 Only - NO SUBSTITUTIONS

	111
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Econolite 5 Inch Border, Aluminum, Black Non-Louvered 5 Section with 3 Inch 3M Tape Border - Econolite P45-01 Only - NO SUBSTITUTIONS

	Group 12 - Price Lines 112 through 114

	112
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, McCain Aluminum Black Non-Louvered 3 Section with 3 Inch 3M Tape Border - McCain HP Only - NO SUBSTITUTIONS

	113
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, McCain Aluminum Black Non-Louvered 4 Section with 3 Inch 3M Tape Border - McCain HP Only - NO SUBSTITUTIONS

	114
	Miscellaneous Signal Products Devices, Backplate - 12" Signal, Mccain Aluminum Black Non-Louvered 5 Section with 3 Inch 3M Tape Border - McCain HP Only - NO SUBSTITUTIONS

	Group 13 - Price Lines 117 through 121

	117
	Traffic Signals and Equipment Traffic Signal Cable 2/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	118
	Traffic Signals and Equipment Traffic Signal Cable 5/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	119
	 Traffic Signals and Equipment Traffic Signal Cable 7/c #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	120
	Traffic Signals and Equipment Traffic Signal Cable 10/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	121
	Traffic Signals and Equipment Traffic Signal Cable 14/C #14 AWG, as per NJDOT Spec. BME-TS-CABLE, Dated July 1, 2008

	Group 14 - Price Lines 122 and 123

	122
	Hand/Man Pedestrian Signal Head, as per NJDOT Spec. BMEO-LED-H/M-PSH- Dated: 09/16/2014 and Bid Solicitation Specifications

	123
	Hand/Man Pedestrian Signal Head, as per NJDOT Spec. BMEO-LED-H/M-PSM- Dated: 09/16/2014 and Bid Solicitation Specifications

	  Group 15 - Price Lines 124 through 126

	124
	Red, Amber, Green LED Module for Optically Programmed Traffic Signal Red Module, as per NJDOT Spec. BMEO-OP-RAG Dated 01/16/2014 and Bid Solicitation Specifications

	125
	Red, Amber, Green LED Module for Optically Programmed Traffic Signal Amber Module, as per NJDOT Spec. BMEO-OP-RAG Dated 01/16/2014 and Bid Solicitation Specifications

	126
	Red, Amber, Green LED Module for Optically Programmed Traffic Signal Green Module, as per NJDOT Spec. BMEO-OP-RAG Dated 01/16/2014 and Bid Solicitation Specifications



Bidders must bid on all price lines contained within the Group.  If a Bidder does not bid on all price lines within the Group, its Quote will be considered non-responsive for that Group.

If a product bid on a price line within the group is deemed non-responsive, the entire group that price line item is part of will be deemed non-responsive, as these price lines were grouped to create a single award, with the intent that all price lines in the group will be awarded.

A Bidder is not required to bid on all Groups on the State-Supplied Price Sheet in order to be considered responsive.  

Price line items are grouped for Quote evaluation purposes only.  Upon Contract award, Using Agencies will be able to order any price lines within the Groups individually.

For Individual Price Lines – Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139:

	Price Line #
	
Description

	Individual Price Lines -  Price Lines 3 and 4

	3
	Traffic Signal Indication Parts Scoop Visor – 12 Inch, as per NJDOT Spec. # BME-TS-Scoop Visor, Dated May 31, 2018

	4
	Geometrically Programmed Louver, Plastic 12 Inch Indication as per NJDOT Spec. & NJDOT Sketch # 1 (Attachment #5), Pelco GL-1010 Only - NO SUBSTITUTIONS

	Individual Price Lines -  Price Lines 7 and 8

	7
	Traffic Signal Indication Parts Traffic Signal Indication - Hand/Man (Housing Only) 16" X 18" as per NJDOT Spec. No. BME-TS-Hand/Man Dated May 25, 2010

	8
	Traffic Signal Indication/Parts Visor Screen (Egg Crate) for 16 "X 18" Indication as per NJDOT Spec. No. BME-TS-VSEC Dated May 31, 2018

	Individual Price Lines -  Price Lines 11 through 30

	11
	Traffic Signal Hangers Brackets Sign Bracket, as per 2007 Standard Electrical Details T-4507 

	12
	Traffic Signal Hangers Brackets Sign Bracket Offset Type, as per 2007 Standard Electrical Details T-4507

	13
	Traffic Signal Hangers Brackets Adapter- Pedestal (Slip Fitter) with Brass Chase Nipple as per 2007 Standard Electrical Details T-0607 and T-0707

	14
	Traffic Signal Hangers Brackets Adapter- Pedestal (Offset Slip Fitter) with Brass Chase Nipple as per NJDOT Sketch #2 (Attachment #5) - NO SUBSTITUTIONS

	15
	Traffic Signal Hangers Brackets Band Bracket Assembly- Mid Arm 8-12” Indication 2007 Standard Electrical  Details T-2107, Pelco AS-116-3-29-SS Only - NO SUBSTITUTIONS

	16
	Traffic Signal Hanger Bracket Cable Bracket Assembly – Mid Arm 8-12” Indication 2007 Standard Electrical Details T-2107, Pelco AS-125-3-29-SS Only - NO SUBSTITUTIONS

	17
	Traffic Signal Hanger Bracket Band Bracket Assembly – Mid Arm- 8-12” Indication 2007 Standard Electrical Details T-2107, Pelco AS-103-3-29-SS Only - NO SUBSTITUTIONS

	18
	Traffic Signal Hanger Bracket Cable Bracket Assembly- Mid Arm 8 -12” Indication 2007 Standard Electrical Details T-2107, Pelco AS-151-3-29-SS Only - NO SUBSTITUTIONS

	19
	Traffic Signal Hangers Brackets Clevis- H Mast Arms 2007 Standard Electrical Details T-0407 Universal  Joint 

	20
	Traffic Signal Hangers Brackets Mast Arm Slip Fitter 2007 Standard Electrical Details T-0407 Mast Arm Slip Fitter 

	21
	Traffic Signal Hangers Brackets Universal Joint & Wire Outlet with SS Hardware 2007 Standard Electrical Details T-0407 Universal Joint and Wire Outlet

	22
	Traffic Signal Hangers Brackets Pedestrian Hinge Clamp Assembly for Approx. 7-1/2” Diameter Pole with 12” Standard Nipple 2007 Standard Electrical Details T-0607

	23
	Traffic Signal Hangers Brackets Pedestrian Hinge Clamp Assembly for Approx. 9-1/2” Diameter Pole with 12” Standard Nipple, 2007 Standard Electrical Details T-0607

	24
	Traffic Signal Hangers Brackets Pedestrian Cast Clamp Assembly for Approx. 9-1/2” Diameter Pole with 12” Standard Nipple, 2007 Standard Electrical Details T-0607

	25
	Traffic Signal Hangers Brackets Pedestrian Cast Clamp for Approx. 9-1/2” Diameter Pole with 12” Standard Nipple, 2007 Standard Electrical Details T-0607

	26
	Traffic Signal Hangers Brackets Two-Way Bracket Assembly with T-Bar 2007 Standard Electrical Details T-0507 Hollow Spider for 2-Way Assembly & T-Bar 

	27
	Traffic Signal Hangers Brackets Three-Way Bracket Assembly 2007 Standard Electrical Details T-0507 Hollow Spider for 3-Way Assembly

	28
	Traffic Signal Hangers Brackets Four-Way Bracket Assembly 2007 Standard Electrical Details T-0507 Hollow Spider for 4-Way Assembly

	29
	Traffic Signal Hangers Brackets Pole Clamp Assembly, Hinge Strap Type with 12” Standard Nipple, 2007 Standard Electrical Details T-0607 Pole Clamp Assembly, Hinge Strap Type

	30
	Traffic Signal Hangers Brackets Traffic Signal Safety Chain 2007 Standard Electrical Details T-0307 and T-0907

	Individual Price Lines - Price Lines 89 and 90

	89
	Cabinets and Cabinet Hardware Meter Cabinet, Composite Carlon Part #C2420A4 Only - NO SUBSTITUTIONS

	90
	Cabinets and Cabinet Hardware Controller Cabinet, Lock & Keys S591, as per NJDOT Sketch #8  (Attachment #5), CCL Products A55481RS: Right Hand, Dead Bolt Only - NO SUBSTITUTIONS

	Individual Price Lines- Price Lines 96 through 100

	96
	Signal Control Devices, Detector (Microwave), as per NJDOT Spec. Drawing Model TC-26B

	97
	Signal Control Devices, Detector (Microwave), as per NJDOT Spec. Drawing Model TC-30

	98
	Signal Control Devices, Loop Detector – 4 Channel, as per NJDOT Spec. EB-LD-3

	99
	Signal Control Devices, Detector Card, as per NJDOT Spec. EB-LD-CARD

	100
	Signal Control Devices, Uninterruptible Power System- 850 Watts, as per NJDOT Spec. #BME-UPS-1, Dated 9/22/2014

	Individual Price Lines – Price Lines 115 and 116

	115
	Miscellaneous Signal Products Devices, GPS Time Reference - Garmin Only - NO SUBSTITUTIONS

	116
	Miscellaneous Signal Products Devices, GPS Time Reference - Eltec Time Sync 1-GPS Only - NO SUBSTITUTIONS

	Individual Price Lines – Price Lines 127 and 128

	127
	Indication LED Solar Beacon Assembly 12” Amber, as per NJDOT Spec. BMEO-LED-SFB Dated 09/16/2014 and Bid Solicitation Specifications

	128
	Adjustable Face Vehicle Traffic Control Aluminum Signal Head (Housing Only 3-12” Sections), as per NJDOT Spec. BMEO-TSH-AL, Dated 1/16/2014 and the Bid Solicitation Specifications

	Individual Price Lines - Price Lines 129 through 139

	129
	Lighting Poles Arms, Bases Black Lighting Arm Assembly as per NJDOT Sketch #12 (Attachment #5)

	130
	Generator Auxiliary Cabinet (GAC) as per Bose GAC-Alpha Dated January 24, 2024, Alpha Only - NO SUBSTITUTIONS

	131
	Generator Auxiliary Cabinet (GAC), as per Bose-GAC-Other Dated January 24, 2024

	132
	Audible Push Button System 8 APS and Control Unit – Polara INS23TNO-Y WITH iCCU-S2 Only - NO SUBSTITUTIONS

	133
	Audible Push Button System 8 APS and Control Unit – Campbell WiAAPS APC 501-0910C - NO SUBSTITUTIONS

	134
	Pedestrian Pole Assembly, as per NJDOT Sketch #13 (Attachment #5) Only - NO SUBSTITUTIONS

	135
	Pedestrian Pole Assembly, as per NJDOT Sketch #13 (Attachment #5)

	136
	Traffic Signal Pole Assembly, as per NJDOT Sketch #14 (Attachment #5) Only - NO SUBSTITUTIONS

	137
	Traffic Signal Pole Assembly, as per NJDOT Sketch #14 (Attachment #5)

	138
	Econolite Cobalt Signal Controller - NO SUBSTITUTIONS

	139
	Trafficware Commander Signal Controller - NO SUBSTITUTIONS



For evaluation purposes, Bidders will be ranked from lowest to highest for the Individual Price Lines (Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139) according to the Quote prices located on the State-Supplied Price Sheet accompanying this Bid Solicitation.

For Individual Price Lines – Price Lines 140 through 154:

	Price Line #
	
Description

	Individual Price Lines – Percentage Discount or Markup from the Brand Manufacturer’s Price List/Catalog Pricing - Price Lines 140 through 154

	140
	Polara Brand Only – Price List - NO SUBSTITUTIONS

	141
	General Fasteners (Any Brand) – Price List 

	142
	Campbell Brand Only – Price List - NO SUBSTITUTIONS

	143
	Econolite Signal Controller Brand Only – Price List - NO SUBSTITUTIONS

	144
	Trafficware Signal Controller Brand Only – Price List - NO SUBSTITUTIONS

	145
	Gridsmart Brand Only – Price List - NO SUBSTITUTIONS

	146
	Miovision Brand Only – Price List - NO SUBSTITUTIONS

	147
	Wavetronix Brand Only – Price List - NO SUBSTITUTIONS

	148
	2-Way Assemblies Components - Pelco Inc. Brand Only - Price List  - NO SUBSTITUTIONS

	149
	Audible Push Button System Components – Polara Brand Only – Price List - NO SUBSTITUTIONS

	150
	Audible Push Button System Components - Campbell Brand Only – Price List - NO SUBSTITUTIONS

	151
	Aeroflex Back Plate - Pelco Inc. Brand Only  - Price List - NO SUBSTITUTIONS

	152
	Alpha Brand Only – Price List - NO SUBSTITUTIONS

	153
	1-Way Assemblies Components - Pelco Inc. Brand Only – Price List - NO SUBSTITUTIONS

	154
	Beacon-4-Life Brand Only – Price List - NO SUBSTITUTIONS



For Price Lines 140 through 154, the State intends to make multiple awards for each Price Line to all of the responsive Bidders.  The Using Agency will calculate the costs based on the percentage discount or markup awarded and the fixed pricing contained in the price list/catalog.  

[bookmark: _Toc118513841][bookmark: _Toc400531551][bookmark: _Toc428534023][bookmark: _Toc32310745][bookmark: _Toc161140971]8.10    QUOTE DISCREPANCIES
In evaluating Quotes, discrepancies between words and figures will be resolved in favor of words.  Discrepancies between Unit Prices and totals of Unit Prices will be resolved in favor of Unit Prices.  Discrepancies in the multiplication of units of work and Unit Prices will be resolved in favor of the Unit Prices.  Discrepancies between the indicated total of multiplied Unit Prices and units of work and the actual total will be resolved in favor of the actual total.  Discrepancies between the indicated sum of any column of figures and the correct sum thereof will be resolved in favor of the correct sum of the column of figures.

[bookmark: _Toc118513842][bookmark: _Toc400531553][bookmark: _Toc428534025][bookmark: _Toc32310747][bookmark: _Toc161140972]8.11    NEGOTIATION
Not applicable to this procurement.

[bookmark: _Toc161140973]8.12    BEST AND FINAL OFFER (BAFO) 
The Procurement Bureau may invite one (1) Bidder or multiple Bidders to submit a Best and Final Offer (BAFO). Said invitation will establish the time and place for submission of the BAFO. Any BAFO that does not result in more advantageous pricing to the State will not be considered, and the State will evaluate the Bidder’s most advantageous previously submitted pricing.

The Division may conduct more than one (1) round of BAFO in order to attain the best value for the State. 

BAFOs will be conducted only in those circumstances where it is deemed by the Procurement Bureau or Director to be in the State’s best interests and to maximize the State’s ability to get the best value.  Therefore, the Bidder is advised to submit its best technical and price Quote in response to this Bid Solicitation since the State may, after evaluation, make a Contract award based on the content of the initial submission 

If the Procurement Bureau contemplates BAFOs, Quote prices will not be publicly read at the Quote opening.  Only the name and address of each Bidder will be publicly announced at the Quote opening.

[bookmark: _Toc32310748][bookmark: _Toc161140974]8.13    “REQUEST FOR REVISION” WITHIN NJSTART
The State may request a revision of the Bidder’s Quote within NJSTART. The Bidder shall respond to the “Request for Revision” only for the reason(s) identified by the State. Any changes made by a Bidder to the Quote other than as requested by the State shall be considered null and void. 

[bookmark: _Toc400531554][bookmark: _Toc428534026][bookmark: _Toc32310749][bookmark: _Toc161140975]8.14    POOR PERFORMANCE
A Bidder with a history of performance problems may be bypassed for consideration of an award issued as a result of this Bid Solicitation. The following materials may be reviewed to determine Bidder performance:  
A. Contract cancellations for cause pursuant to State of New Jersey Standard Terms and Conditions Section 5.7(B); 
B. Information contained in Contractor performance records; 
C. Information obtained from audits or investigations conducted by a local, state or federal agency of the Bidder’s work experience; 
D. Current licensure, registration, and/or certification status and relevant history thereof; or 
E. Bidder’s status or rating with established business/financial reporting services, as applicable.  

Bidders should note that this list is not exhaustive.

[bookmark: _Toc161140976]8.15    RECOMMENDATION FOR AWARD 
After the evaluation of the submitted Quotes is complete, the Procurement Bureau will recommend to the Director for award, the responsible Bidder(s) whose Quote, conforming to this Bid Solicitation, is most advantageous to the State, price and other factors considered.  The Director may accept, reject or modify the recommendation of the Procurement Bureau.

[bookmark: _Toc400531561][bookmark: _Toc428534033][bookmark: _Toc32310756][bookmark: _Toc161140977]8.16    CONTRACT AWARD
Contract award(s) will be made with reasonable promptness by written notice to those responsible Bidders, whose Quotes, conforming to this Bid Solicitation, are most advantageous to the State, price, and other factors considered.  Any or all Quotes may be rejected when the State Treasurer or the Director determines that it is in the public interest to do so.  Contract awards will be publicly posted under the relevant contract number and available on NJSTART.

The State intends to make Contract awards in accordance with Section 8.9 of this Bid Solicitation as follows:

· One award for Group 1 (sum of Price Lines 1 and 2)
· One award for Group 2 (sum of Price Lines 5 and 6)
· One award for Group 3 (sum of Price Lines 9 and 10)
· One award for Group 4 (sum of Price Lines 31 through 64)
· One award for Group 5 (sum of Price Lines 65 through 78)
· One award for Group 6 (sum of Price Lines 79 through 88)
· One award for Group 7 (sum of Price Lines 91 through 95)
· One award for Group 8 (sum of Price Lines 101 and 102)
· One award for Group 9 (sum of Price Lines 103 and 104)
· One award for Group 10 (sum of Price Lines 105 through 108)
· One award for Group 11 (sum of Price Lines 109 through 111)
· Once award for Group 12 (sum of Price Lines 112 through 114)
· Once award for Group 13 (sum of Price Lines 117 through 121)
· Once award for Group 14 (sum of Price Lines 122 and 123)
· Once award for Group 15 (sum of Price Lines 124 through 126)

For Individual Price Lines – Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139:

For Price Lines 3, 4, 7, 8, 11 through 30, 89, 90, 96 through 100, 115, 116, 127, 128, and 129 through 139, the State intends to make one award for each individual price line based on the lowest Unit Price bid.

For Individual Price Lines – Price Lines 140 through 154:

For Price Lines 140 through 154, the State intends to make multiple awards for each Price Line to all of the responsive Bidders.  The Using Agency will calculate the costs based on the percentage discount or markup awarded and the fixed pricing contained in the price list/catalog.  Please refer to Bid Solicitation Section 4.55 for the Contract Method of Operation for Price Lines 140 through 154.



[bookmark: _Toc161140978]GLOSSARY

[bookmark: _Toc161140979]9.1    CROSSWALK

	Current DPP Template Term
	Equivalent Statutory, Regulatory NJSTART and/or Legacy Term

	Bid Solicitation 
	Request For Proposal (RFP)/Solicitation

	Bid Amendment 
	Addendum

	Contract 
	Master Blanket Purchase Order (Blanket/Blanket P.O.)

	Contract Amendment 
	Change Order

	Administrative Change Order
	Change Order

	Quote
	Proposal/Bid

	Contractor
	Vendor/Contractor

	Bidder
	Bidder/Contractor



[bookmark: _Toc161140980]9.2    DEFINITIONS
Unless otherwise specified in the Bid Solicitation, the following definitions will be part of any Contract awarded, or order placed, as a result of this Bid Solicitation.  Note that not all definitions included here apply to all Bid Solicitations.
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Acceptance – The written confirmation by the Using Agency that Contractor has completed a Deliverable according to the specified requirements.

Administrative Change Order – A unilateral administrative modification to the Contract in the NJSTART system by the Division. Administrative Change Orders are not to be considered formal Contract Amendments.
All-Inclusive Hourly Rate – An hourly rate comprised of all direct and indirect costs including, but not limited to: labor costs, overhead, fee or profit, clerical support, travel expenses, per diem, safety equipment, materials, supplies, managerial support and all documents, forms, and reproductions thereof.  This rate also includes portal-to-portal expenses as well as per diem expenses such as food.

Apparel – means any clothing, headwear, linens or fabric.  

Apparel Contracts – include all purchases, rentals or other acquisition of apparel products by the State of New Jersey, including authorizations by the State of New Jersey for contractors to sell apparel products through cash allowances or vouchers issued by the State of New Jersey, and license agreements with a public body.

Apparel Production – includes the cutting and manufacturing of apparel products performed by the contractor or by any subcontractors, but not including the production of supplies or sundries such as buttons, zippers, and thread.

Approved Products – Those products that have been identified in Bid Solicitation as meeting Using Agency needs and confirmed as meeting product specifications.

Best and Final Offer or BAFO – Pricing timely submitted by a Bidder upon invitation by the Procurement Bureau after Quote opening, with or without prior discussion or negotiation.

Bid or Bid Solicitation – The documents which establish the bidding and Contract requirements and solicits Quotes to meet the needs of the Using Agencies as identified herein, and includes the Bid Solicitation, State of New Jersey Standard Terms and Conditions (SSTC), State-Supplied Price Sheet, Attachments, and Bid Amendments.

Bid Amendment – Written clarification or revision to this Bid Solicitation issued by the Division. Bid Amendments, if any, will be issued prior to Quote opening.

Bid Opening Date – The date Quotes will be opened for evaluation and closed to further Quote submissions.

Bid Security - means a guarantee, in a form acceptable to the Division, that the bidder, if selected, will accept the contract as bid; otherwise, the bidder or, as applicable, its guarantor will be liable for the amount of the loss suffered by the State, which loss may be partially or completely recovered by the State in exercising its rights against the instrument of bid security.

Bidder – An entity offering a Quote in response to the Division’s Bid Solicitation.

Breach of Security – as defined by N.J.S.A. 56:8-161, means unauthorized access to electronic files, media, or data containing Personal Data that compromises the security, confidentiality, or integrity of Personal Data when access to the Personal Data has not been secured by encryption or by any other method or technology that renders the Personal Data unreadable or unusable.  Good faith acquisition of Personal Data by an employee or agent of the Provider for a legitimate business purpose is not a Breach of Security, provided that the Personal Data is not used for a purposes unrelated to the business or subject to further unauthorized disclosure.  

Business Day – Any weekday, excluding Saturdays, Sundays, State legal holidays, and State-mandated closings unless otherwise indicated.

Calendar Day – Any day, including Saturdays, Sundays, State legal holidays, and State-mandated closings unless otherwise indicated.

Commercial off the Shelf Software or COTS – Software provided by Provider that is commercially available and that can be used with little or no modification.

Customized Software – COTS that is adapted or configured by Provider to meet specific requirements of the Authorized Purchaser that differ from the standard requirements of the base product. For the avoidance of doubt, “Customized Software” is not permitted to be sold to the State under the scope of this Contract.

Contract – The Contract consists of the State of NJ Standard Terms and Conditions (SSTC), the Bid Solicitation, the responsive Quote submitted by a responsible Bidder as accepted by the State, the notice of award, any Best and Final Offer, any subsequent written document memorializing the agreement, any modifications to any of these documents approved by the State and any attachments, Bid Amendment or other supporting documents, or post-award documents including Contract Amendments agreed to by the State and the Contractor, in writing.

Contract Amendment – An amendment, alteration, or modification of the terms of a Contract between the State and the Contractor(s). A Contract Amendment is not effective until it is signed and approved in writing by the person with the appropriate signing authority.  Contract Amendments are tracked using Change Orders in NJSTART. Please note that Administrative Change Orders (see definition above) are not considered Contract Amendments.  

Contractor – The Bidder awarded a Contract resulting from this Bid Solicitation.

Contractor Intellectual Property – Any intellectual property that is owned by Contractor and contained in or necessary for the use of the Deliverables or which the Contractor makes available for the State to use as part of the work under the Contract.  Contractor Intellectual Property includes COTS or Customized Software owned by Contractor, Contractor’s technical documentation, and derivative works and compilations of any Contractor Intellectual Property.

Cooperative Purchasing Program – The Division’s intrastate program that provides procurement-related assistance to New Jersey local governmental entities and boards of education, State and county colleges and other public entities having statutory authority to utilize select State Contract s issued by the Division, pursuant to the provisions of N.J.S.A. 52:25-16.1 et seq.
Cooperative Purchasing Participants – These participants include quasi-State entities, counties, municipalities, school districts, volunteer fire departments, first aid squads, independent institutions of higher learning, County colleges, and State colleges.

Days After Receipt of Order (ARO) – The number of calendar days ‘After Receipt of Order’ in which the Using Agency will receive the ordered materials and/or services.

Dealer/Distributor – A Company authorized by a Bidder or Contractor as having the contractual ability to accept and fulfill orders and receive payments directly on behalf of the Contractor that is awarded a Contract.  Any authorized Dealer/Distributor must agree to all terms and conditions contained within the Bid Solicitation and must agree to provide all products and services in accordance with the Contract specifications, terms, conditions and pricing.  

Deliverable – Goods, products, Services and Work Product that Contractor is required to deliver to the State under the Contract.

Director – Director, Division of Purchase and Property, Department of the Treasury, who by statutory authority is the Chief Contracting Officer for the State of New Jersey; or the Director’s designee.

Disabled Veterans’ Business - means a business which has its principal place of business in the State, is independently owned and operated and at least 51% of which is owned and controlled by persons who are disabled veterans or a business which has its principal place of business in this State and has been officially verified by the United States Department of Veterans Affairs as a service disabled veteran-owned business for the purposes of department contracts pursuant to federal law.  N.J.S.A. 52:32-31.2.

Disabled Veterans’ Business Set-Aside Contract – means a Contract for goods, equipment, construction or services which is designated as a Contract with respect to which bids are invited and accepted only from disabled veterans’ businesses, or a portion of a Contract when that portion has been so designated.  N.J.S.A. 52:32-31.2.

Discount – The standard price reduction applied by the Bidder to all items.

Division – The Division of Purchase and Property.

Equivalent Products – Products offered other than those identified as an Approved Product in this Bid Solicitation that meet the specifications herein. Equivalent Products will be evaluated to ensure that they meet all technical, nutritional, and packaging specifications herein as part of the Quote evaluation process.

Evaluation Committee – A group of individuals or a Division staff member assigned by the Director to review and evaluate Quotes submitted in response to this Bid Solicitation and recommend a Contract award to the Director.

Firm Fixed Price – A price that is all-inclusive of direct cost and indirect costs, including, but not limited to, direct labor costs, overhead, fee or profit, clerical support, equipment, materials, supplies, managerial (administrative) support, all documents, reports, forms, travel, reproduction and any other costs.

Hardware – Includes computer equipment and any Software provided with the Hardware that is necessary for the Hardware to operate.

Internet of Things (IoT) – the network of physical devices, vehicles, home appliances and other items embedded with electronics, software, sensors, actuators, and network connectivity which enables these objects to connect and exchange data.

Intrastate cooperative purchasing participants – refers to political subdivisions, volunteer fire departments and first aid squads, and independent institutions of higher education and school districts pursuant to N.J.S.A. 52:25-16.1 et seq., State and county colleges pursuant to N.J.S.A. 18A:64-60 and 18A:64A-25.9, quasi-State agencies and independent authorities pursuant to N.J.S.A. 52:27B-56.1, and other New Jersey public entities having statutory authority to utilize select State contracts issued by the Division.

Joint Venture – A business undertaking by two (2) or more entities to share risk and responsibility for a specific project.

Life cycle assessment – The comprehensive examination of a product’s environmental and economic aspects and potential impacts throughout its lifetime, including raw material extraction, transportation, manufacturing, use and disposal.

Life cycle cost – The amortized total cost of a product, including capital costs, installation costs, operating costs, maintenance costs, and disposal costs discounted over the lifetime of the product.

Master Blanket Purchase Order (Blanket/Blanket P.O.) – A Term Contract that allows repeated purchases from an awarded contract.

Materials in Solid Waste – Material found in the various components of the solid waste stream. General, solid waste has several components, such as municipal solid waste (MSW), construction and demolition debris (C&D), and nonhazardous industrial waste.  Under RCRA Section 6002, EPA considers materials recovered from any component of the solid waste stream when designating items containing Recovered Materials.

May – Denotes that which is permissible or recommended, not mandatory.

Mobile Device – means any device used by Provider that can move or transmit data, including but not limited to laptops, hard drives, and flash drives.

Must – Denotes that which is a mandatory requirement.  

Net Purchases – means the total gross purchases, less credits, taxes, regulatory fees and separately stated shipping charges not included in unit prices, made by Intrastate Cooperative Purchasing Participants, regardless of whether or not NJSTART is used as part of the purchase process.

No Bid – The Bidder is not submitting a price Quote for an item on a price line.

No Charge – The Bidder will supply an item on a price line free of charge.

Non-Public Data – means data, other than Personal Data, that is not subject to distribution to the public as public information. Non-Public Data is data that is identified by the State as non-public information or otherwise deemed to be sensitive and confidential by the State because it contains information that is exempt by statute, ordinance or administrative rule from access by the general public as public information.

Percentage Discount or Markup – The percentage bid applied as a Markup or a Discount to a firm, fixed price contained within a price list/catalog. 

Performance Security – means a guarantee, executed subsequent to award, in a form acceptable to the Division, that the successful bidder will complete the contract as agreed and that the State will be protected from loss in the event the contractor fails to complete the contract as agreed.

Personal Data means – 
“Personal Information” as defined in N.J.S.A. 56:8-161, means an individual’s first name or first initial and last name linked with any one or more of the following data elements: (1) Social Security number, (2) driver’s license number or State identification card number or (3) account number or credit or debit card number, in combination with any required security code, access code, or password that would permit access to an individual’s financial account.  Dissociated data that, if linked would constitute Personal Information is Personal Information if the means to link the dissociated were accessed in connection with access to the dissociated data.  Personal Information shall not include publicly available information that is lawfully made available to the general public from federal, state or local government records, or widely distributed media; and/or 

Data, either alone or in combination with other data, that includes information relating to an individual that identifies the person or entity by name, identifying number, mark or description that can be readily associated with a particular individual and which is not a public record, including but not limited to, Personally Identifiable Information (PII); government-issued identification numbers (e.g., Social Security, driver’s license, passport); Protected Health Information (PHI) as that term is defined in the regulations adopted pursuant to the Health Insurance Portability and Accountability Act of 1996, P.L. No. 104-191 (1996) and found in 45 CFR Parts 160 to 164 and defined below; and Education Records, as that term is defined in the Family Educational Rights and Privacy Act (FERPA), 20 U.S.C. § 1232g.

Personally Identifiable Information or PII - as defined by the U.S. Department of Commerce, National Institute of Standards and Technology, means any information about an individual maintained by an agency, including (1) any information that can be used to distinguish or trace an individual’s identity, such as name, social security number, date and place of birth, mother’s maiden name, or biometric records; and (2) any other information that is linked or linkable to an individual, such as medical, educational, financial, and employment information.

Post-Consumer Material – Material or finished product that has served its intended use and has been diverted or recovered from waste destined for disposal, having completed its life as a consumer item.  Post-Consumer Materials are part of the broader category of Recovered Materials.

Pre-Consumer Material – Materials generated in manufacturing and converting processes, such as manufacturing scrap and trimmings/cuttings.

Price List/Catalog – A document published by a manufacturer, resellers, Dealers, or Distributors that typically contains product descriptions, a list of products with fixed prices to which a Bidder’s percentage discount or markup bid is applied. 

Procurement Bureau (Bureau) – The Division unit responsible for the preparation, advertisement, and issuance of Bid Solicitations, for the tabulation of Quotes and for recommending award(s) of Contract(s) to the Director and the Deputy Director.

Project – The undertakings or services that are the subject of this Bid Solicitation.

Protected Health Information or PHI – has the same meaning as the term is defined in the regulations adopted pursuant to the Health Insurance Portability and Accountability Act of 1996, P.L. No. 104-191 (1996) and found in 45 CFR Parts 160 to 164 means Individually Identifiable Health Information (as defined below) transmitted by electronic media, maintained in electronic media, or transmitted or maintained in any other form or medium. PHI excludes education records covered by the Family Educational Rights and Privacy Act (FERPA), as amended, 20 U.S.C. 1232g, records described at 20 U.S.C. 1232g(a)(4)(B)(iv) and employment records held by a covered entity in its role as employer. The term “Individually Identifiable Health Information” has the same meaning as the term is defined in the regulations adopted pursuant to the Health Insurance Portability and Accountability Act of 1996, P.L. No. 104-191 (1996) and found in 45 CFR Parts 160 to 164 and means information that is a subset of Protected Health Information, including demographic information collected from an individual, and (1) is created or received by a health care provider, health plan, employer or health care clearinghouse; and (2) relates to the past, present or future physical or mental health or condition of an individual; the provision of health care to an individual; or the past, present or future payment for the provision of health care to an individual; and (a) that identifies the individual; or (b) with respect to which there is a reasonable basis to believe the information can be used to identify the individual.

Purchases - means the total gross purchases, less credits, taxes, regulatory fees and separately stated shipping charges not included in unit prices, made regardless of whether or not NJSTART is used as part of the purchase process.

Quasi-State Agency – is any agency, commission, board, authority or other such governmental entity which is established and is allocated to a State department or any bi-state governmental entity of which the State of New Jersey is a member, as defined in N.J.S.A. 52:27B-56.1, provided that any sale to any such bi-state governmental entity is for use solely within the State of New Jersey.

Quick Reference Guides (QRGs) – Informational documents which provide Vendors with step-by-step instructions to navigate the NJSTART eProcurement System. QRGs are available on the NJSTART Vendor Support Page.

Quote – Bidder’s timely response to the Bid Solicitation including, but not limited to, technical Quote, price Quote including Best and Final Offer, any licenses, forms, certifications, clarifications, negotiated documents, and/or other documentation required by the Bid Solicitation.

Quote Opening Date – The date Quotes will be opened for evaluation and closed to further Quote submissions.

Recovered Material – Waste material and byproduct that have been recovered or diverted from solid waste, but does not include materials and byproducts generated from, and commonly reused within, an original manufacturing process.

Recycling – The series of activities, including collection, separation, and processing, by which products or other materials are recovered from the solid waste stream for use in the form of raw materials in the manufacture of new products other than fuel for producing heat or power by combustion.
Recyclability – The ability of a product or material to be recovered from, or otherwise diverted from, the solid waste stream for the purpose of recycling.

Retainage – The amount withheld from the Contractor payment that is retained and subsequently released upon satisfactory completion of performance milestones by the Contractor.

Revision – A response to a BAFO request or a requested clarification of the Bidder’s Quote. 

RMAN – Recovered Materials Advisory Notices provide purchasing guidance and recommendations for Recovered and Post-Consumer Material content levels for designated items. 

Security Incident – means the potential access by non-authorized person(s) to Personal Data or Non-Public Data that the Provider believes could reasonably result in the use, disclosure, or access or theft of State’s unencrypted Personal Data or Non-Public Data within the possession or control of the Provider. A Security Incident may or may not turn into a Breach of Security.

Services – Includes, without limitation (i) Information Technology (IT) professional services, (ii) Software and Hardware-related services, including without limitation, installation, configuration, and training, and (iii) Software and Hardware maintenance and support and/or Software and Hardware technical support services. 

Shall – Denotes that which is a mandatory requirement.  

Should – Denotes that which is permissible or recommended, not mandatory.

Small Business – Pursuant to N.J.S.A. 52:32-19, N.J.A.C. 17:13-1.2, and N.J.A.C. 17:13-2.1, “small business” means a business that meets the requirements and definitions of “small business” and has applied for and been approved by the New Jersey Division of Revenue and Enterprise Services, Small Business Registration and M/WBE Certification Services Unit as (i) independently owned and operated, (ii) incorporated or registered in and has its principal place of business in the State of New Jersey; (iii)  has 100 or fewer full-time employees; and has gross revenues falling in one (1) of the six (6) following categories:  
For goods and services - (A) 0 to $500,000 (Category I); (B) $500,001 to $5,000,000 (Category II); and (C) $5,000,001 to $12,000,000, or the applicable federal revenue standards established at 13 CFR 121.201, whichever is higher (Category III). 
For construction services: (A) 0 to $3,000,000 (Category IV); (B) gross revenues that do not exceed 50 percent of the applicable annual revenue standards established at 13 CFR 121.201 (Category V); and (C) gross revenues that do not exceed the applicable annual revenue standards established at CFR 121.201, (Category VI).

Small Business Set-Aside Contract – means (1) a Contract for goods, equipment, construction or services which is designated as a Contract with respect to which bids are invited and accepted only from small businesses, or (2) a portion of a Contract when that portion has been so designated.”  N.J.S.A. 52:32-19.

Software – means, without limitation, computer programs, source codes, routines, or subroutines supplied by Provider, including operating software, programming aids, application programs, application programming interfaces and software products, and includes COTS, unless the context indicates otherwise.  

Software as a Service or SaaS – means the capability provided to a purchaser to use the Provider’s applications running on a cloud infrastructure. The applications are accessible from various client devices through a thin client interface such as a Web browser (e.g., Web-based email) or a program interface. The purchaser does not manage or control the underlying cloud infrastructure, including network, servers, operating systems, storage or even individual application capabilities, with the possible exception of limited user-specific application configuration settings.

State – The State of New Jersey.

State Confidential Information – shall consist of State Data and State Intellectual Property  supplied by the State, any information or data gathered by the Contractor in fulfillment of the Contract and any analysis thereof (whether in fulfillment of the Contract or not).

State Contract Manager or SCM – The individual, responsible for the approval of all deliverables, i.e., tasks, sub-tasks or other work elements in the Scope of Work.  The SCM cannot direct or approve a Contract Amendment.

State Data – means all data and metadata created or in any way originating with the State, and all data that is the output of computer processing of or other electronic manipulation of any data that was created by or in any way originated with the State, whether such data or output is stored on the State’s hardware, the Provider’s hardware or exists in any system owned, maintained or otherwise controlled by the State or by the Provider.  State Data includes Personal Data and Non-Public Data.

State Intellectual Property – Any intellectual property that is owned by the State.  State Intellectual Property includes any derivative works and compilations of any State Intellectual Property.

State Price Sheet or State-Supplied Price Sheet – the bidding document created by the State and attached to this Bid Solicitation on which the Bidder submits its Quote pricing as is referenced and described in the Bid Solicitation.   

Subtasks – Detailed activities that comprise the actual performance of a task.

Subcontractor – An entity having an arrangement with a Contractor, whereby the Contractor uses the products and/or services of that entity to fulfill some of its obligations under its State Contract, while retaining full responsibility for the performance of all  Contractor's obligations under the Contract, including payment to the Subcontractor.  The Subcontractor has no legal relationship with the State, only with the Contractor.

Task – A discrete unit of work to be performed.

Third Party Intellectual Property – Any intellectual property owned by parties other than the State or Contractor and contained in or necessary for the use of the Deliverables.  Third Party Intellectual Property includes COTS owned by Third Parties, and derivative works and compilations of any Third Party Intellectual Property. 

Unit Cost or Unit Price – All-inclusive, firm fixed price charged by the Bidder for a single unit identified on a price line.

US CERT – United States Computer Emergency Readiness Team.

USEPA – United States Environmental Protection Agency.

Using Agency[ies] – A State department or agency, a quasi-State governmental entity, or an Intrastate Cooperative Purchasing participant, authorized to purchase products and/or services under a Contract procured by the Division. 

Vendor – Either the Bidder or the Contractor.

Work Product – Every invention, modification, discovery, design, development, customization, configuration, improvement, process, Software program, work of authorship, documentation, formula, datum, technique, know how, secret, or intellectual property right whatsoever or any interest therein (whether patentable or not patentable or registerable under copyright or similar statutes or subject to analogous protection) that is specifically made, conceived, discovered, or reduced to practice by Contractor or Contractor’s subcontractors or a third party engaged by Contractor or its subcontractor pursuant to the Contract Notwithstanding anything to the contrary in the preceding sentence, Work Product does not include State Intellectual Property, Contractor Intellectual Property or Third Party Intellectual Property. 









[bookmark: _Toc161140981]9.3    CONTRACT-SPECIFIC DEFINITIONS
Unless otherwise specified in the Bid Solicitation, the following Contract-specific definitions will be part of any Contract awarded, or order placed, as a result of this Bid Solicitation.  

dB – Decibel.

FCC – Federal Communications Commission.  Federal Communications Commission | The United States of America (fcc.gov)

ITE – Institute of Transportation Engineering 
Institute of Transportation Engineers - ITE
http://www.ite.org/ 

KHz – Kilohertz.

LED – Light Emitting Diode.

LF – Linear Foot/Linear Feet.

MUTCD - Manual on Uniform Traffic Control Devices 
Manual on Uniform Traffic Control Devices (MUTCD) - FHWA
http://mutcd.fhwa.dot.gov/ 

NEMA – National Electrical Manufacturers Association http://www.nema.org/pages/default.aspx 

VTCSH – Vehicle Traffic Control Signal Heads
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