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March 25, 2021


To:	All Interested Vendors {Bidders}


Re:	Bid Solicitation # 20DPP00537
T2732 – Maintenance/Repair and Replacement Services - Portable Commercial Mobile Generator


Quote Submission Due Date: March 31, 2021 (2:00 p.m. Eastern Time)
Revised Quote Submission Due Date: April 14, 2021  (2:00 p.m. Eastern Time)


Bid Amendment #2


The following constitutes Bid Amendment #2 to the above referenced Bid Solicitation:
  

· This Bid Amendment includes answers to questions;

· Revises the Quote Submission Due Date to April 14, 2021  (2:00 p.m. Eastern Time); and

· Please note that for all additions, deletions, clarifications and modifications to the Bid Solicitation, please refer to the Revised Bid Solicitation titled, “T2732 REVISED Bid Solicitation 3.25.21”.

It is the sole responsibility of the Vendor {Bidder} to be knowledgeable of all of the additions, deletions, clarifications, and modifications to the Bid Solicitation and/or the New Jersey Standard Terms and Conditions relative to this Bid Solicitation as set forth in all Bid Amendments. 

All other instructions, terms, and conditions of the Bid Solicitation shall remain the same.
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Bid Solicitation #20DPP00537
T2732 – Maintenance/Repair and Replacement Services - Portable Commercial Mobile Generator

Answers to Questions

Where applicable, each question references the appropriate Bid Solicitation section. 

	#
	Bid Solicitation
Section Reference
	Question (Bolded) and Answer 

	1
	PDF Documents
	When trying to open a Portable Document Format (PDF) I am receiving an error message and am unable to access the PDF. How should I proceed?

It is recommended that users utilize Internet Explorer to view PDFs. Certain PDF forms cannot be opened in the Chrome or Firefox built in PDF views that are enabled by default. If using Chrome or Firefox it is recommended that the file is downloaded instead by clicking the download button in the upper right-hand corner of the browser after an error message is received. An alternative option is to disable the built in PDF viewers in Chrome or Firefox.
 

	2
	Quote Submission
	Should I check that I have properly completed and attached all of the required documents with my submitted Quote?

Yes. Prior to the Quote Opening Deadline, a Vendor {Bidder} should review the documents comprising the submitted Quote to ensure that all of the required documents have been completed and attached. Oftentimes a Quote is deemed non-responsive because a Vendor {Bidder} fails to attach a required form or attaches a blank form. To review a submitted Quote a Vendor {Bidder} should log into NJSTART and review each document attached to the Quote submission. Instructions on how to review a submitted Quote can be found in the Quick Reference Guide entitled ‘How to Review a Submitted Quote’ which is available on the NJSTART Vendor Support Page under Vendor References Guides.


	3
	Section 3.4              Preventative Maintenance
	On the Pricing Sheet, for the first price line, it reads all inclusive price rate and a task for the category but, the bid specs indicate hourly rate for all inclusive? Is the pricing for the task for a Major Maintenance, Minor Maintenance, hourly pricing?

The State clarifies in the Revised Bid Solicitation that Bid Solicitation Section 3.4 Preventative Maintenance shall be an “…all-inclusive task rate for all preventative maintenance work…”. 

Price Line 1 on The State-Supplied Price Sheet shall remain unchanged as “All Inclusive Task Rate for Preventative Maintenance”.

The pricing for all preventative maintenance shall be in accordance with Bid Solicitation Section 3.4 which states, “The Vendor {Contractor} shall charge the awarded all-inclusive task rate for all preventative maintenance work…”. 

For the purposes of this Bid Solicitation, the State considers the work referenced in Section 3.4 as a single task, including but not limited to the following:

A. Cost for the removal of existing generator/cabinetry (If applicable);

B. Replacement of engine oils;

C. Replacement of all oil fluids/lubricants;

D. Replacement of all fuel filters;

E. Replacement of all air filters;

F. Inspection of fan belt;

1. Adjustment of fan belt tension when required;

G. Inspection of coolant levels and conditions;

1. Addition of coolant when required;

H. Inspect for fluid leaks;

I. Inspect starting system;

J. Inspect charging system;

K. Test pre-heat operations;

L. Inspect breaker panel;

M. Test the remote start and stop functions;

N. Inspect generator mounting;

O. Installation of existing surrounding cabinetry; and

P. Proper disposal of any used parts, fluids, or byproducts resulting from preventative maintenance services.


Note: This question has been paraphrased in the interest of readability and clarity.


	4
	General
	Is there a Portable kw range we are to supply or can it be any kw size?

The State currently requires a minimum kilowatt (kW) range between 5,000kW to 24,000kW. However, the State anticipates adding additional generators with greater kW range in the future that the Vendor {Contractor} will be required to be able to meet.


	5
	Section 3.4 Preventative Maintenance
	A) All inclusive means inclusive of the maintenance work listed on the scope of work and not all inclusive of any repair, correct? B) The Maintenance Cost includes cost for the removal of existing generator/cabinetry? C) Wouldn't that factor more into the Installation and Purchasing as generator removal would need to be part of that process?

A) Preventative maintenance and repair work are independent services and each have their own applicable price line. 

[bookmark: _Toc355709006][bookmark: _Toc400531490][bookmark: _Toc428533961][bookmark: _Toc63248413]Please refer to Bid Solicitation Section 2.2 General Definitions and Section 2.3 Blanket P.O. Specific Definition/Acroyms for specified terms including “All-Inclusive Hourly Rate” and “All-Inclusive Task Rate”. 

In addition, and in accordance with Bid Solicitation Section 3.2 Hourly Rate, “Vendor {Contractors} shall perform services at the applicable awarded all-inclusive hourly rate or all-inclusive task rate (where specified) for the services as specified in Bid Solicitation Section 3.0, Scope of Work”.

B) Yes, if removal of existing generator cabintry is required in order to perform preventative maintenance than it would fall under the task rate for preventative maintenance. However, removal of cabintry is not expected to be required for the performance of most preventative maintenance tasks. 

C) Certain aspects of performing preventative maintenance service and new generator installation may be similar, however, work for each of these services shall remain separate and independent of each other. Payment shall be based upon the appropriate price line for the service being requested and performed.  

Note: This question has been paraphrased in the interest of readability and clarity.
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